## FRICLOSS
Liquid Process Equipment
2026-07-29 16:23
ESTIMATED FRICTION LOSS CALCULATION
Customer- | CIP Supply |  |  | Ref-
[5 empty] | Equivalent |  |  | 1.003
| Input Data |  | Fittings | Qty | Length (ft) |  | 0.26531 | 0.007
[7 empty] | 0.26772 | 0.0071
Fluid= | Water |  | # 90 Ell's = | 2 | 1.8143 |  | 0.27011 | 0.0072
GPM= | 100 |  | #45 Ell's = | 5 | 2.2679 |  | 0.27249 | 0.0073
I.D.= | 2.87 | in. | #Tee Branch Flow = | 0 | 0 |  | 0.27486 | 0.0074
Length (Ft) = | 25 | ft. | #Tee Line Flow = | 2 | 3.283 |  | 0.27722 | 0.0075
Viscosity (cps) = | 100 | cp. | # Globe Valve = | 0 | 0 |  | 0.27956 | 0.0076
SP.GR.= | 1.05 |  | # Gate Valve = | 0 | 0
Vertical rise= | 0 | ft. | # Swing Check Vlv = | 0 | 0 |  | 0.28189 | 0.0077
|  |  | # Angle Valve = | 0 | 0 |  | 0.28421 | 0.0078
[7 empty] | 0.28652 | 0.0079
|  |  |  | Total (ft): | 7.3652 |  | 0.28881 | 0.008
RESULTS
Head Loss = | #VALUE! | ft | Head loss = | (f * L * V^2) / (2 * ID * Gc) + Vrise
Pressure Drop = | #VALUE! | psig | Press. drop = | (Head Loss * SP.GR) / 2.31 |  |  | 0.2911 | 0.0081
[7 empty] | 0.29337 | 0.0082
[7 empty] | 0.29563 | 0.0083
[7 empty] | 0.29788 | 0.0084
Total Length (L) = | #VALUE! | ft | Total Length = Eqiv. Len + Length |  |  |  | 0.30013 | 0.0085
kinimatic Viscosity(v) = | 0.0010261 | ft^2/sec |  |  |  |  | 0.30236 | 0.0086
ID = | 0.23917 | ft |  |  |  |  | 0.30458 | 0.0087
Flow Area= | 0.044925 | ft^2 |  |  |  |  | 0.30679 | 0.0088
Flow= | 0.2228 | cfs |  |  |  |  | 0.30899 | 0.0089
Velocity (V) = | 4.9593 | fps |  |  |  |  | 0.31118 | 0.009
Shear Rate = | 165.8213 | [5 empty] | 0.31336 | 0.0091
Reynolds Number(Re) = | 1155.952 |  | Re = V * ID / v |  |  |  | 0.31553 | 0.0092
Roughness: (e) = | 1.5e-05 | ft | Standard value for polish SS tubing |  |  |  | 0.3177 | 0.0093
Gc = | 32.17 | ft/sec^2 | Gravitational constant |  |  |  | 0.31985 | 0.0094
e / ID= | 6.2718e-05 | [5 empty] | 0.32199 | 0.0095
Friction Factor: (f) = | 0.055366 |  | Friction factor has been calculated utilizing an iterative |  |  |  | 0.32413 | 0.0096
|  |  | method, base upon the Darcy Weisbach charts. |  |  | 0.32626 | 0.0097
[6 empty] | 0.32837 | 0.0098
[6 empty] | 0.33048 | 0.0099
[6 empty] | 0.33259 | 0.01
[6 empty] | 0.33468 | 0.0101
[6 empty] | 0.33676 | 0.0102
[6 empty] | 0.33884 | 0.0103
[6 empty] | 0.34091 | 0.0104
[6 empty] | 0.34297 | 0.0105
[6 empty] | 0.34502 | 0.0106
[6 empty] | 0.34707 | 0.0107
[6 empty] | 0.3491 | 0.0108
[6 empty] | 0.35113 | 0.0109
[6 empty] | 0.35316 | 0.011
[6 empty] | 0.35517 | 0.0111
[6 empty] | 0.35718 | 0.0112
[6 empty] | 0.35918 | 0.0113
[6 empty] | 0.36117 | 0.0114
[6 empty] | 0.36316 | 0.0115
[6 empty] | 0.36514 | 0.0116
[6 empty] | 0.36712 | 0.0117
[6 empty] | 0.36908 | 0.0118
[6 empty] | 0.37104 | 0.0119
[6 empty] | 0.373 | 0.012
[6 empty] | 0.37494 | 0.0121
[6 empty] | 0.37688 | 0.0122
[6 empty] | 0.37882 | 0.0123
[6 empty] | 0.38075 | 0.0124
[6 empty] | 0.38267 | 0.0125
[6 empty] | 0.38458 | 0.0126
[6 empty] | 0.38649 | 0.0127
[6 empty] | 0.3884 | 0.0128
[6 empty] | 0.39029 | 0.0129
[6 empty] | 0.39219 | 0.013
[6 empty] | 0.39407 | 0.0131
[6 empty] | 0.39595 | 0.0132
[6 empty] | 0.39783 | 0.0133
[6 empty] | 0.3997 | 0.0134
[6 empty] | 0.40156 | 0.0135
[6 empty] | 0.40342 | 0.0136
[6 empty] | 0.40527 | 0.0137
[6 empty] | 0.40712 | 0.0138
[6 empty] | 0.40896 | 0.0139
[6 empty] | 0.4108 | 0.014
[6 empty] | 0.41263 | 0.0141
[6 empty] | 0.41445 | 0.0142
[6 empty] | 0.41627 | 0.0143
[6 empty] | 0.41809 | 0.0144
[6 empty] | 0.4199 | 0.0145
[6 empty] | 0.42171 | 0.0146
[6 empty] | 0.42351 | 0.0147
[6 empty] | 0.4253 | 0.0148
[6 empty] | 0.42709 | 0.0149
[6 empty] | 0.42888 | 0.015
[6 empty] | 0.43066 | 0.0151
[6 empty] | 0.43244 | 0.0152
[6 empty] | 0.43421 | 0.0153
[6 empty] | 0.43598 | 0.0154
[6 empty] | 0.43774 | 0.0155
[6 empty] | 0.4395 | 0.0156
[6 empty] | 0.44125 | 0.0157
[6 empty] | 0.443 | 0.0158
[6 empty] | 0.44475 | 0.0159
[6 empty] | 0.44649 | 0.016
[6 empty] | 0.44822 | 0.0161
[6 empty] | 0.44996 | 0.0162
[6 empty] | 0.45168 | 0.0163
[6 empty] | 0.45341 | 0.0164
[6 empty] | 0.45513 | 0.0165
[6 empty] | 0.45684 | 0.0166
[6 empty] | 0.45855 | 0.0167
[6 empty] | 0.46026 | 0.0168
[6 empty] | 0.46196 | 0.0169
[6 empty] | 0.46366 | 0.017
[6 empty] | 0.46535 | 0.0171
[6 empty] | 0.46704 | 0.0172
[6 empty] | 0.46873 | 0.0173
[6 empty] | 0.47041 | 0.0174
[6 empty] | 0.47209 | 0.0175
[6 empty] | 0.47377 | 0.0176
[6 empty] | 0.47544 | 0.0177
[6 empty] | 0.4771 | 0.0178
[6 empty] | 0.47877 | 0.0179
[6 empty] | 0.48043 | 0.018
[6 empty] | 0.48208 | 0.0181
[6 empty] | 0.48374 | 0.0182
[6 empty] | 0.48538 | 0.0183
[6 empty] | 0.48703 | 0.0184
[6 empty] | 0.48867 | 0.0185
[6 empty] | 0.49031 | 0.0186
[6 empty] | 0.49194 | 0.0187
[6 empty] | 0.49357 | 0.0188
[6 empty] | 0.4952 | 0.0189
[6 empty] | 0.49683 | 0.019
[6 empty] | 0.49845 | 0.0191
[6 empty] | 0.50006 | 0.0192
[6 empty] | 0.50168 | 0.0193
[6 empty] | 0.50329 | 0.0194
[6 empty] | 0.50489 | 0.0195
[6 empty] | 0.5065 | 0.0196
[6 empty] | 0.5081 | 0.0197
[6 empty] | 0.50969 | 0.0198
[6 empty] | 0.51129 | 0.0199
[6 empty] | 0.51288 | 0.02
[6 empty] | 0.51447 | 0.0201
[6 empty] | 0.51605 | 0.0202
[6 empty] | 0.51763 | 0.0203
[6 empty] | 0.51921 | 0.0204
[6 empty] | 0.52078 | 0.0205
[6 empty] | 0.52236 | 0.0206
[6 empty] | 0.52392 | 0.0207
[6 empty] | 0.52549 | 0.0208
[6 empty] | 0.52705 | 0.0209
[6 empty] | 0.52861 | 0.021
[6 empty] | 0.53017 | 0.0211
[6 empty] | 0.53172 | 0.0212
[6 empty] | 0.53327 | 0.0213
[6 empty] | 0.53482 | 0.0214
[6 empty] | 0.53636 | 0.0215
[6 empty] | 0.53791 | 0.0216
[6 empty] | 0.53945 | 0.0217
[6 empty] | 0.54098 | 0.0218
[6 empty] | 0.54251 | 0.0219
[6 empty] | 0.54404 | 0.022
[6 empty] | 0.54557 | 0.0221
[6 empty] | 0.5471 | 0.0222
[6 empty] | 0.54862 | 0.0223
[6 empty] | 0.55014 | 0.0224
[6 empty] | 0.55165 | 0.0225
[6 empty] | 0.55317 | 0.0226
[6 empty] | 0.55468 | 0.0227
[6 empty] | 0.55619 | 0.0228
[6 empty] | 0.55769 | 0.0229
[6 empty] | 0.5592 | 0.023
[6 empty] | 0.5607 | 0.0231
[6 empty] | 0.56219 | 0.0232
[6 empty] | 0.56369 | 0.0233
[6 empty] | 0.56518 | 0.0234
[6 empty] | 0.56667 | 0.0235
[6 empty] | 0.56816 | 0.0236
[6 empty] | 0.56964 | 0.0237
[6 empty] | 0.57113 | 0.0238
[6 empty] | 0.57261 | 0.0239
[6 empty] | 0.57408 | 0.024
[6 empty] | 0.57556 | 0.0241
[6 empty] | 0.57703 | 0.0242
[6 empty] | 0.5785 | 0.0243
[6 empty] | 0.57997 | 0.0244
[6 empty] | 0.58143 | 0.0245
[6 empty] | 0.5829 | 0.0246
[6 empty] | 0.58436 | 0.0247
[6 empty] | 0.58581 | 0.0248
[6 empty] | 0.58727 | 0.0249
[6 empty] | 0.58872 | 0.025
[6 empty] | 0.59017 | 0.0251
[6 empty] | 0.59162 | 0.0252
[6 empty] | 0.59307 | 0.0253
[6 empty] | 0.59451 | 0.0254
[6 empty] | 0.59595 | 0.0255
[6 empty] | 0.59739 | 0.0256
[6 empty] | 0.59883 | 0.0257
[6 empty] | 0.60026 | 0.0258
[6 empty] | 0.60169 | 0.0259
[6 empty] | 0.60312 | 0.026
[6 empty] | 0.60455 | 0.0261
[6 empty] | 0.60598 | 0.0262
[6 empty] | 0.6074 | 0.0263
[6 empty] | 0.60882 | 0.0264
[6 empty] | 0.61024 | 0.0265
[6 empty] | 0.61166 | 0.0266
[6 empty] | 0.61307 | 0.0267
[6 empty] | 0.61448 | 0.0268
[6 empty] | 0.61589 | 0.0269
[6 empty] | 0.6173 | 0.027
[6 empty] | 0.61871 | 0.0271
[6 empty] | 0.62011 | 0.0272
[6 empty] | 0.62151 | 0.0273
[6 empty] | 0.62291 | 0.0274
[6 empty] | 0.62431 | 0.0275
[6 empty] | 0.62571 | 0.0276
[6 empty] | 0.6271 | 0.0277
[6 empty] | 0.62849 | 0.0278
[6 empty] | 0.62988 | 0.0279
[6 empty] | 0.63127 | 0.028
[6 empty] | 0.63265 | 0.0281
[6 empty] | 0.63404 | 0.0282
[6 empty] | 0.63542 | 0.0283
[6 empty] | 0.6368 | 0.0284
[6 empty] | 0.63818 | 0.0285
[6 empty] | 0.63955 | 0.0286
[6 empty] | 0.64093 | 0.0287
[6 empty] | 0.6423 | 0.0288
[6 empty] | 0.64367 | 0.0289
[6 empty] | 0.64504 | 0.029
[6 empty] | 0.6464 | 0.0291
[6 empty] | 0.64776 | 0.0292
[6 empty] | 0.64913 | 0.0293
[6 empty] | 0.65049 | 0.0294
[6 empty] | 0.65185 | 0.0295
[6 empty] | 0.6532 | 0.0296
[6 empty] | 0.65456 | 0.0297
[6 empty] | 0.65591 | 0.0298
[6 empty] | 0.65726 | 0.0299
[6 empty] | 0.65861 | 0.03
[6 empty] | 0.65996 | 0.0301
[6 empty] | 0.6613 | 0.0302
[6 empty] | 0.66264 | 0.0303
[6 empty] | 0.66399 | 0.0304
[6 empty] | 0.66533 | 0.0305
[6 empty] | 0.66666 | 0.0306
[6 empty] | 0.668 | 0.0307
[6 empty] | 0.66934 | 0.0308
[6 empty] | 0.67067 | 0.0309
[6 empty] | 0.672 | 0.031
[6 empty] | 0.67333 | 0.0311
[6 empty] | 0.67466 | 0.0312
[6 empty] | 0.67598 | 0.0313
[6 empty] | 0.67731 | 0.0314
[6 empty] | 0.67863 | 0.0315
[6 empty] | 0.67995 | 0.0316
[6 empty] | 0.68127 | 0.0317
[6 empty] | 0.68259 | 0.0318
[6 empty] | 0.6839 | 0.0319
[6 empty] | 0.68522 | 0.032
[6 empty] | 0.68653 | 0.0321
[6 empty] | 0.68784 | 0.0322
[6 empty] | 0.68915 | 0.0323
[6 empty] | 0.69045 | 0.0324
[6 empty] | 0.69176 | 0.0325
[6 empty] | 0.69306 | 0.0326
[6 empty] | 0.69437 | 0.0327
[6 empty] | 0.69567 | 0.0328
[6 empty] | 0.69697 | 0.0329
[6 empty] | 0.69826 | 0.033
[6 empty] | 0.69956 | 0.0331
[6 empty] | 0.70085 | 0.0332
[6 empty] | 0.70215 | 0.0333
[6 empty] | 0.70344 | 0.0334
[6 empty] | 0.70473 | 0.0335
[6 empty] | 0.70602 | 0.0336
[6 empty] | 0.7073 | 0.0337
[6 empty] | 0.70859 | 0.0338
[6 empty] | 0.70987 | 0.0339
[6 empty] | 0.71115 | 0.034
[6 empty] | 0.71243 | 0.0341
[6 empty] | 0.71371 | 0.0342
[6 empty] | 0.71499 | 0.0343
[6 empty] | 0.71626 | 0.0344
[6 empty] | 0.71754 | 0.0345
[6 empty] | 0.71881 | 0.0346
[6 empty] | 0.72008 | 0.0347
[6 empty] | 0.72135 | 0.0348
[6 empty] | 0.72262 | 0.0349
[6 empty] | 0.72389 | 0.035
[6 empty] | 0.72515 | 0.0351
[6 empty] | 0.72641 | 0.0352
[6 empty] | 0.72768 | 0.0353
[6 empty] | 0.72894 | 0.0354
[6 empty] | 0.7302 | 0.0355
[6 empty] | 0.73146 | 0.0356
[6 empty] | 0.73271 | 0.0357
[6 empty] | 0.73397 | 0.0358
[6 empty] | 0.73522 | 0.0359
[6 empty] | 0.73647 | 0.036
[6 empty] | 0.73772 | 0.0361
[6 empty] | 0.73897 | 0.0362
[6 empty] | 0.74022 | 0.0363
[6 empty] | 0.74147 | 0.0364
[6 empty] | 0.74271 | 0.0365
[6 empty] | 0.74396 | 0.0366
[6 empty] | 0.7452 | 0.0367
[6 empty] | 0.74644 | 0.0368
[6 empty] | 0.74768 | 0.0369
[6 empty] | 0.74892 | 0.037
[6 empty] | 0.75015 | 0.0371
[6 empty] | 0.75139 | 0.0372
[6 empty] | 0.75262 | 0.0373
[6 empty] | 0.75386 | 0.0374
[6 empty] | 0.75509 | 0.0375
[6 empty] | 0.75632 | 0.0376
[6 empty] | 0.75755 | 0.0377
[6 empty] | 0.75877 | 0.0378
[6 empty] | 0.76 | 0.0379
[6 empty] | 0.76122 | 0.038
[6 empty] | 0.76245 | 0.0381
[6 empty] | 0.76367 | 0.0382
[6 empty] | 0.76489 | 0.0383
[6 empty] | 0.76611 | 0.0384
[6 empty] | 0.76733 | 0.0385
[6 empty] | 0.76854 | 0.0386
[6 empty] | 0.76976 | 0.0387
[6 empty] | 0.77097 | 0.0388
[6 empty] | 0.77219 | 0.0389
[6 empty] | 0.7734 | 0.039
[6 empty] | 0.77461 | 0.0391
[6 empty] | 0.77582 | 0.0392
[6 empty] | 0.77703 | 0.0393
[6 empty] | 0.77823 | 0.0394
[6 empty] | 0.77944 | 0.0395
[6 empty] | 0.78064 | 0.0396
[6 empty] | 0.78185 | 0.0397
[6 empty] | 0.78305 | 0.0398
[6 empty] | 0.78425 | 0.0399
[6 empty] | 0.78545 | 0.04
[6 empty] | 0.78665 | 0.0401
[6 empty] | 0.78784 | 0.0402
[6 empty] | 0.78904 | 0.0403
[6 empty] | 0.79023 | 0.0404
[6 empty] | 0.79143 | 0.0405
[6 empty] | 0.79262 | 0.0406
[6 empty] | 0.79381 | 0.0407
[6 empty] | 0.795 | 0.0408
[6 empty] | 0.79619 | 0.0409
[6 empty] | 0.79737 | 0.041
[6 empty] | 0.79856 | 0.0411
[6 empty] | 0.79974 | 0.0412
[6 empty] | 0.80093 | 0.0413
[6 empty] | 0.80211 | 0.0414
[6 empty] | 0.80329 | 0.0415
[6 empty] | 0.80447 | 0.0416
[6 empty] | 0.80565 | 0.0417
[6 empty] | 0.80683 | 0.0418
[6 empty] | 0.808 | 0.0419
[6 empty] | 0.80918 | 0.042
[6 empty] | 0.81035 | 0.0421
[6 empty] | 0.81153 | 0.0422
[6 empty] | 0.8127 | 0.0423
[6 empty] | 0.81387 | 0.0424
[6 empty] | 0.81504 | 0.0425
[6 empty] | 0.81621 | 0.0426
[6 empty] | 0.81738 | 0.0427
[6 empty] | 0.81854 | 0.0428
[6 empty] | 0.81971 | 0.0429
[6 empty] | 0.82087 | 0.043
[6 empty] | 0.82203 | 0.0431
[6 empty] | 0.8232 | 0.0432
[6 empty] | 0.82436 | 0.0433
[6 empty] | 0.82552 | 0.0434
[6 empty] | 0.82668 | 0.0435
[6 empty] | 0.82783 | 0.0436
[6 empty] | 0.82899 | 0.0437
[6 empty] | 0.83015 | 0.0438
[6 empty] | 0.8313 | 0.0439
[6 empty] | 0.83245 | 0.044
[6 empty] | 0.83361 | 0.0441
[6 empty] | 0.83476 | 0.0442
[6 empty] | 0.83591 | 0.0443
[6 empty] | 0.83706 | 0.0444
[6 empty] | 0.8382 | 0.0445
[6 empty] | 0.83935 | 0.0446
[6 empty] | 0.8405 | 0.0447
[6 empty] | 0.84164 | 0.0448
[6 empty] | 0.84278 | 0.0449
[6 empty] | 0.84393 | 0.045
[6 empty] | 0.84507 | 0.0451
[6 empty] | 0.84621 | 0.0452
[6 empty] | 0.84735 | 0.0453
[6 empty] | 0.84849 | 0.0454
[6 empty] | 0.84962 | 0.0455
[6 empty] | 0.85076 | 0.0456
[6 empty] | 0.8519 | 0.0457
[6 empty] | 0.85303 | 0.0458
[6 empty] | 0.85416 | 0.0459
[6 empty] | 0.8553 | 0.046
[6 empty] | 0.85643 | 0.0461
[6 empty] | 0.85756 | 0.0462
[6 empty] | 0.85869 | 0.0463
[6 empty] | 0.85981 | 0.0464
[6 empty] | 0.86094 | 0.0465
[6 empty] | 0.86207 | 0.0466
[6 empty] | 0.86319 | 0.0467
[6 empty] | 0.86432 | 0.0468
[6 empty] | 0.86544 | 0.0469
[6 empty] | 0.86656 | 0.047
[6 empty] | 0.86769 | 0.0471
[6 empty] | 0.86881 | 0.0472
[6 empty] | 0.86993 | 0.0473
[6 empty] | 0.87104 | 0.0474
[6 empty] | 0.87216 | 0.0475
[6 empty] | 0.87328 | 0.0476
[6 empty] | 0.87439 | 0.0477
[6 empty] | 0.87551 | 0.0478
[6 empty] | 0.87662 | 0.0479
[6 empty] | 0.87773 | 0.048
[6 empty] | 0.87885 | 0.0481
[6 empty] | 0.87996 | 0.0482
[6 empty] | 0.88107 | 0.0483
[6 empty] | 0.88218 | 0.0484
[6 empty] | 0.88328 | 0.0485
[6 empty] | 0.88439 | 0.0486
[6 empty] | 0.8855 | 0.0487
[6 empty] | 0.8866 | 0.0488
[6 empty] | 0.88771 | 0.0489
[6 empty] | 0.88881 | 0.049
[6 empty] | 0.88991 | 0.0491
[6 empty] | 0.89101 | 0.0492
[6 empty] | 0.89211 | 0.0493
[6 empty] | 0.89321 | 0.0494
[6 empty] | 0.89431 | 0.0495
[6 empty] | 0.89541 | 0.0496
[6 empty] | 0.89651 | 0.0497
[6 empty] | 0.8976 | 0.0498
[6 empty] | 0.8987 | 0.0499
[6 empty] | 0.89979 | 0.05
[6 empty] | 0.90088 | 0.0501
[6 empty] | 0.90198 | 0.0502
[6 empty] | 0.90307 | 0.0503
[6 empty] | 0.90416 | 0.0504
[6 empty] | 0.90525 | 0.0505
[6 empty] | 0.90634 | 0.0506
[6 empty] | 0.90742 | 0.0507
[6 empty] | 0.90851 | 0.0508
[6 empty] | 0.9096 | 0.0509
[6 empty] | 0.91068 | 0.051
[6 empty] | 0.91177 | 0.0511
[6 empty] | 0.91285 | 0.0512
[6 empty] | 0.91393 | 0.0513
[6 empty] | 0.91502 | 0.0514
[6 empty] | 0.9161 | 0.0515
[6 empty] | 0.91718 | 0.0516
[6 empty] | 0.91826 | 0.0517
[6 empty] | 0.91933 | 0.0518
[6 empty] | 0.92041 | 0.0519
[6 empty] | 0.92149 | 0.052
[6 empty] | 0.92256 | 0.0521
[6 empty] | 0.92364 | 0.0522
[6 empty] | 0.92471 | 0.0523
[6 empty] | 0.92579 | 0.0524
[6 empty] | 0.92686 | 0.0525
[6 empty] | 0.92793 | 0.0526
[6 empty] | 0.929 | 0.0527
[6 empty] | 0.93007 | 0.0528
[6 empty] | 0.93114 | 0.0529
[6 empty] | 0.93221 | 0.053
[6 empty] | 0.93327 | 0.0531
[6 empty] | 0.93434 | 0.0532
[6 empty] | 0.93541 | 0.0533
[6 empty] | 0.93647 | 0.0534
[6 empty] | 0.93754 | 0.0535
[6 empty] | 0.9386 | 0.0536
[6 empty] | 0.93966 | 0.0537
[6 empty] | 0.94072 | 0.0538
[6 empty] | 0.94178 | 0.0539
[6 empty] | 0.94284 | 0.054
[6 empty] | 0.9439 | 0.0541
[6 empty] | 0.94496 | 0.0542
[6 empty] | 0.94602 | 0.0543
[6 empty] | 0.94708 | 0.0544
[6 empty] | 0.94813 | 0.0545
[6 empty] | 0.94919 | 0.0546
[6 empty] | 0.95024 | 0.0547
[6 empty] | 0.95129 | 0.0548
[6 empty] | 0.95235 | 0.0549
[6 empty] | 0.9534 | 0.055
[6 empty] | 0.95445 | 0.0551
[6 empty] | 0.9555 | 0.0552
[6 empty] | 0.95655 | 0.0553
[6 empty] | 0.9576 | 0.0554
[6 empty] | 0.95865 | 0.0555
[6 empty] | 0.95969 | 0.0556
[6 empty] | 0.96074 | 0.0557
[6 empty] | 0.96179 | 0.0558
[6 empty] | 0.96283 | 0.0559
[6 empty] | 0.96388 | 0.056
[6 empty] | 0.96492 | 0.0561
[6 empty] | 0.96596 | 0.0562
[6 empty] | 0.967 | 0.0563
[6 empty] | 0.96804 | 0.0564
[6 empty] | 0.96908 | 0.0565
[6 empty] | 0.97012 | 0.0566
[6 empty] | 0.97116 | 0.0567
[6 empty] | 0.9722 | 0.0568
[6 empty] | 0.97324 | 0.0569
[6 empty] | 0.97428 | 0.057
[6 empty] | 0.97531 | 0.0571
[6 empty] | 0.97635 | 0.0572
[6 empty] | 0.97738 | 0.0573
[6 empty] | 0.97841 | 0.0574
[6 empty] | 0.97945 | 0.0575
[6 empty] | 0.98048 | 0.0576
[6 empty] | 0.98151 | 0.0577
[6 empty] | 0.98254 | 0.0578
[6 empty] | 0.98357 | 0.0579
[6 empty] | 0.9846 | 0.058
[6 empty] | 0.98563 | 0.0581
[6 empty] | 0.98666 | 0.0582
[6 empty] | 0.98768 | 0.0583
[6 empty] | 0.98871 | 0.0584
[6 empty] | 0.98973 | 0.0585
[6 empty] | 0.99076 | 0.0586
[6 empty] | 0.99178 | 0.0587
[6 empty] | 0.99281 | 0.0588
[6 empty] | 0.99383 | 0.0589
[6 empty] | 0.99485 | 0.059
[6 empty] | 0.99587 | 0.0591
[6 empty] | 0.99689 | 0.0592
[6 empty] | 0.99791 | 0.0593
[6 empty] | 0.99893 | 0.0594
[6 empty] | 0.99995 | 0.0595
[6 empty] | 1.001 | 0.0596
[6 empty] | 1.002 | 0.0597
[6 empty] | 1.003 | 0.0598
[6 empty] | 1.004 | 0.0599
[6 empty] | 1.005 | 0.06
[6 empty] | 1.006 | 0.0601
[6 empty] | 1.0071 | 0.0602
[6 empty] | 1.0081 | 0.0603
[6 empty] | 1.0091 | 0.0604
[6 empty] | 1.0101 | 0.0605
[6 empty] | 1.0111 | 0.0606
[6 empty] | 1.0121 | 0.0607
[6 empty] | 1.0131 | 0.0608
[6 empty] | 1.0141 | 0.0609
[6 empty] | 1.0151 | 0.061
[6 empty] | 1.0161 | 0.0611
[6 empty] | 1.0172 | 0.0612
[6 empty] | 1.0182 | 0.0613
[6 empty] | 1.0192 | 0.0614
[6 empty] | 1.0202 | 0.0615
[6 empty] | 1.0212 | 0.0616
[6 empty] | 1.0222 | 0.0617
[6 empty] | 1.0232 | 0.0618
[6 empty] | 1.0242 | 0.0619
[6 empty] | 1.0252 | 0.062
[6 empty] | 1.0262 | 0.0621
[6 empty] | 1.0272 | 0.0622
[6 empty] | 1.0282 | 0.0623
[6 empty] | 1.0292 | 0.0624
[6 empty] | 1.0302 | 0.0625
[6 empty] | 1.0312 | 0.0626
[6 empty] | 1.0322 | 0.0627
[6 empty] | 1.0332 | 0.0628
[6 empty] | 1.0342 | 0.0629
[6 empty] | 1.0352 | 0.063
[6 empty] | 1.0362 | 0.0631
[6 empty] | 1.0371 | 0.0632
[6 empty] | 1.0381 | 0.0633
[6 empty] | 1.0391 | 0.0634
[6 empty] | 1.0401 | 0.0635
[6 empty] | 1.0411 | 0.0636
[6 empty] | 1.0421 | 0.0637
[6 empty] | 1.0431 | 0.0638
[6 empty] | 1.0441 | 0.0639
[6 empty] | 1.0451 | 0.064
[6 empty] | 1.0461 | 0.0641
[6 empty] | 1.047 | 0.0642
[6 empty] | 1.048 | 0.0643
[6 empty] | 1.049 | 0.0644
[6 empty] | 1.05 | 0.0645
[6 empty] | 1.051 | 0.0646
[6 empty] | 1.052 | 0.0647
[6 empty] | 1.053 | 0.0648
[6 empty] | 1.0539 | 0.0649
[6 empty] | 1.0549 | 0.065
[6 empty] | 1.0559 | 0.0651
[6 empty] | 1.0569 | 0.0652
[6 empty] | 1.0579 | 0.0653
[6 empty] | 1.0588 | 0.0654
[6 empty] | 1.0598 | 0.0655
[6 empty] | 1.0608 | 0.0656
[6 empty] | 1.0618 | 0.0657
[6 empty] | 1.0627 | 0.0658
[6 empty] | 1.0637 | 0.0659
[6 empty] | 1.0647 | 0.066
[6 empty] | 1.0657 | 0.0661
[6 empty] | 1.0666 | 0.0662
[6 empty] | 1.0676 | 0.0663
[6 empty] | 1.0686 | 0.0664
[6 empty] | 1.0696 | 0.0665
[6 empty] | 1.0705 | 0.0666
[6 empty] | 1.0715 | 0.0667
[6 empty] | 1.0725 | 0.0668
[6 empty] | 1.0735 | 0.0669
[6 empty] | 1.0744 | 0.067
[6 empty] | 1.0754 | 0.0671
[6 empty] | 1.0764 | 0.0672
[6 empty] | 1.0773 | 0.0673
[6 empty] | 1.0783 | 0.0674
[6 empty] | 1.0793 | 0.0675
[6 empty] | 1.0802 | 0.0676
[6 empty] | 1.0812 | 0.0677
[6 empty] | 1.0822 | 0.0678
[6 empty] | 1.0831 | 0.0679
[6 empty] | 1.0841 | 0.068
[6 empty] | 1.085 | 0.0681
[6 empty] | 1.086 | 0.0682
[6 empty] | 1.087 | 0.0683
[6 empty] | 1.0879 | 0.0684
[6 empty] | 1.0889 | 0.0685
[6 empty] | 1.0899 | 0.0686
[6 empty] | 1.0908 | 0.0687
[6 empty] | 1.0918 | 0.0688
[6 empty] | 1.0927 | 0.0689
[6 empty] | 1.0937 | 0.069
[6 empty] | 1.0946 | 0.0691
[6 empty] | 1.0956 | 0.0692
[6 empty] | 1.0966 | 0.0693
[6 empty] | 1.0975 | 0.0694
[6 empty] | 1.0985 | 0.0695
[6 empty] | 1.0994 | 0.0696
[6 empty] | 1.1004 | 0.0697
[6 empty] | 1.1013 | 0.0698
[6 empty] | 1.1023 | 0.0699
[6 empty] | 1.1032 | 0.07
[6 empty] | 1.1042 | 0.0701
[6 empty] | 1.1051 | 0.0702
[6 empty] | 1.1061 | 0.0703
[6 empty] | 1.107 | 0.0704
[6 empty] | 1.108 | 0.0705
[6 empty] | 1.1089 | 0.0706
[6 empty] | 1.1099 | 0.0707
[6 empty] | 1.1108 | 0.0708
[6 empty] | 1.1118 | 0.0709
[6 empty] | 1.1127 | 0.071
[6 empty] | 1.1137 | 0.0711
[6 empty] | 1.1146 | 0.0712
[6 empty] | 1.1156 | 0.0713
[6 empty] | 1.1165 | 0.0714
[6 empty] | 1.1175 | 0.0715
[6 empty] | 1.1184 | 0.0716
[6 empty] | 1.1193 | 0.0717
[6 empty] | 1.1203 | 0.0718
[6 empty] | 1.1212 | 0.0719
[6 empty] | 1.1222 | 0.072
[6 empty] | 1.1231 | 0.0721
[6 empty] | 1.124 | 0.0722
[6 empty] | 1.125 | 0.0723
[6 empty] | 1.1259 | 0.0724
[6 empty] | 1.1269 | 0.0725
[6 empty] | 1.1278 | 0.0726
[6 empty] | 1.1287 | 0.0727
[6 empty] | 1.1297 | 0.0728
[6 empty] | 1.1306 | 0.0729
[6 empty] | 1.1315 | 0.073
[6 empty] | 1.1325 | 0.0731
[6 empty] | 1.1334 | 0.0732
[6 empty] | 1.1343 | 0.0733
[6 empty] | 1.1353 | 0.0734
[6 empty] | 1.1362 | 0.0735
[6 empty] | 1.1371 | 0.0736
[6 empty] | 1.1381 | 0.0737
[6 empty] | 1.139 | 0.0738
[6 empty] | 1.1399 | 0.0739
[6 empty] | 1.1409 | 0.074
[6 empty] | 1.1418 | 0.0741
[6 empty] | 1.1427 | 0.0742
[6 empty] | 1.1437 | 0.0743
[6 empty] | 1.1446 | 0.0744
[6 empty] | 1.1455 | 0.0745
[6 empty] | 1.1464 | 0.0746
[6 empty] | 1.1474 | 0.0747
[6 empty] | 1.1483 | 0.0748
[6 empty] | 1.1492 | 0.0749
[6 empty] | 1.1501 | 0.075
[6 empty] | 1.1511 | 0.0751
[6 empty] | 1.152 | 0.0752
[6 empty] | 1.1529 | 0.0753
[6 empty] | 1.1538 | 0.0754
[6 empty] | 1.1548 | 0.0755
[6 empty] | 1.1557 | 0.0756
[6 empty] | 1.1566 | 0.0757
[6 empty] | 1.1575 | 0.0758
[6 empty] | 1.1585 | 0.0759
[6 empty] | 1.1594 | 0.076
[6 empty] | 1.1603 | 0.0761
[6 empty] | 1.1612 | 0.0762
[6 empty] | 1.1621 | 0.0763
[6 empty] | 1.163 | 0.0764
[6 empty] | 1.164 | 0.0765
[6 empty] | 1.1649 | 0.0766
[6 empty] | 1.1658 | 0.0767
[6 empty] | 1.1667 | 0.0768
[6 empty] | 1.1676 | 0.0769
[6 empty] | 1.1685 | 0.077
[6 empty] | 1.1695 | 0.0771
[6 empty] | 1.1704 | 0.0772
[6 empty] | 1.1713 | 0.0773
[6 empty] | 1.1722 | 0.0774
[6 empty] | 1.1731 | 0.0775
[6 empty] | 1.174 | 0.0776
[6 empty] | 1.1749 | 0.0777
[6 empty] | 1.1758 | 0.0778
[6 empty] | 1.1768 | 0.0779
[6 empty] | 1.1777 | 0.078
[6 empty] | 1.1786 | 0.0781
[6 empty] | 1.1795 | 0.0782
[6 empty] | 1.1804 | 0.0783
[6 empty] | 1.1813 | 0.0784
[6 empty] | 1.1822 | 0.0785
[6 empty] | 1.1831 | 0.0786
[6 empty] | 1.184 | 0.0787
[6 empty] | 1.1849 | 0.0788
[6 empty] | 1.1858 | 0.0789
[6 empty] | 1.1867 | 0.079
[6 empty] | 1.1877 | 0.0791
[6 empty] | 1.1886 | 0.0792
[6 empty] | 1.1895 | 0.0793
[6 empty] | 1.1904 | 0.0794
[6 empty] | 1.1913 | 0.0795
[6 empty] | 1.1922 | 0.0796
[6 empty] | 1.1931 | 0.0797
[6 empty] | 1.194 | 0.0798
[6 empty] | 1.1949 | 0.0799
[6 empty] | 1.1958 | 0.08
[6 empty] | 1.1967 | 0.0801
[6 empty] | 1.1976 | 0.0802
[6 empty] | 1.1985 | 0.0803
[6 empty] | 1.1994 | 0.0804
[6 empty] | 1.2003 | 0.0805
[6 empty] | 1.2012 | 0.0806
[6 empty] | 1.2021 | 0.0807
[6 empty] | 1.203 | 0.0808
[6 empty] | 1.2039 | 0.0809
[6 empty] | 1.2048 | 0.081
[6 empty] | 1.2057 | 0.0811
[6 empty] | 1.2065 | 0.0812
[6 empty] | 1.2074 | 0.0813
[6 empty] | 1.2083 | 0.0814
[6 empty] | 1.2092 | 0.0815
[6 empty] | 1.2101 | 0.0816
[6 empty] | 1.211 | 0.0817
[6 empty] | 1.2119 | 0.0818
[6 empty] | 1.2128 | 0.0819
[6 empty] | 1.2137 | 0.082
[6 empty] | 1.2146 | 0.0821
[6 empty] | 1.2155 | 0.0822
[6 empty] | 1.2164 | 0.0823
[6 empty] | 1.2173 | 0.0824
[6 empty] | 1.2181 | 0.0825
[6 empty] | 1.219 | 0.0826
[6 empty] | 1.2199 | 0.0827
[6 empty] | 1.2208 | 0.0828
[6 empty] | 1.2217 | 0.0829
[6 empty] | 1.2226 | 0.083
[6 empty] | 1.2235 | 0.0831
[6 empty] | 1.2244 | 0.0832
[6 empty] | 1.2252 | 0.0833
[6 empty] | 1.2261 | 0.0834
[6 empty] | 1.227 | 0.0835
[6 empty] | 1.2279 | 0.0836
[6 empty] | 1.2288 | 0.0837
[6 empty] | 1.2297 | 0.0838
[6 empty] | 1.2306 | 0.0839
[6 empty] | 1.2314 | 0.084
[6 empty] | 1.2323 | 0.0841
[6 empty] | 1.2332 | 0.0842
[6 empty] | 1.2341 | 0.0843
[6 empty] | 1.235 | 0.0844
[6 empty] | 1.2358 | 0.0845
[6 empty] | 1.2367 | 0.0846
[6 empty] | 1.2376 | 0.0847
[6 empty] | 1.2385 | 0.0848
[6 empty] | 1.2394 | 0.0849
[6 empty] | 1.2402 | 0.085
[6 empty] | 1.2411 | 0.0851
[6 empty] | 1.242 | 0.0852
[6 empty] | 1.2429 | 0.0853
[6 empty] | 1.2437 | 0.0854
[6 empty] | 1.2446 | 0.0855
[6 empty] | 1.2455 | 0.0856
[6 empty] | 1.2464 | 0.0857
[6 empty] | 1.2472 | 0.0858
[6 empty] | 1.2481 | 0.0859
[6 empty] | 1.249 | 0.086
[6 empty] | 1.2499 | 0.0861
[6 empty] | 1.2507 | 0.0862
[6 empty] | 1.2516 | 0.0863
[6 empty] | 1.2525 | 0.0864
[6 empty] | 1.2534 | 0.0865
[6 empty] | 1.2542 | 0.0866
[6 empty] | 1.2551 | 0.0867
[6 empty] | 1.256 | 0.0868
[6 empty] | 1.2568 | 0.0869
[6 empty] | 1.2577 | 0.087
[6 empty] | 1.2586 | 0.0871
[6 empty] | 1.2595 | 0.0872
[6 empty] | 1.2603 | 0.0873
[6 empty] | 1.2612 | 0.0874
[6 empty] | 1.2621 | 0.0875
[6 empty] | 1.2629 | 0.0876
[6 empty] | 1.2638 | 0.0877
[6 empty] | 1.2647 | 0.0878
[6 empty] | 1.2655 | 0.0879
[6 empty] | 1.2664 | 0.088
[6 empty] | 1.2673 | 0.0881
[6 empty] | 1.2681 | 0.0882
[6 empty] | 1.269 | 0.0883
[6 empty] | 1.2699 | 0.0884
[6 empty] | 1.2707 | 0.0885
[6 empty] | 1.2716 | 0.0886
[6 empty] | 1.2724 | 0.0887
[6 empty] | 1.2733 | 0.0888
[6 empty] | 1.2742 | 0.0889
[6 empty] | 1.275 | 0.089
[6 empty] | 1.2759 | 0.0891
[6 empty] | 1.2767 | 0.0892
[6 empty] | 1.2776 | 0.0893
[6 empty] | 1.2785 | 0.0894
[6 empty] | 1.2793 | 0.0895
[6 empty] | 1.2802 | 0.0896
[6 empty] | 1.281 | 0.0897
[6 empty] | 1.2819 | 0.0898
[6 empty] | 1.2828 | 0.0899
[6 empty] | 1.2836 | 0.09
[6 empty] | 1.2845 | 0.0901
[6 empty] | 1.2853 | 0.0902
[6 empty] | 1.2862 | 0.0903
[6 empty] | 1.287 | 0.0904
[6 empty] | 1.2879 | 0.0905
[6 empty] | 1.2888 | 0.0906
[6 empty] | 1.2896 | 0.0907
[6 empty] | 1.2905 | 0.0908
[6 empty] | 1.2913 | 0.0909
[6 empty] | 1.2922 | 0.091
[6 empty] | 1.293 | 0.0911
[6 empty] | 1.2939 | 0.0912
[6 empty] | 1.2947 | 0.0913
[6 empty] | 1.2956 | 0.0914
[6 empty] | 1.2964 | 0.0915
[6 empty] | 1.2973 | 0.0916
[6 empty] | 1.2981 | 0.0917
[6 empty] | 1.299 | 0.0918

## data
DATA
Tube OD Sizes | Gage | Wall Thickness | ID
1/2" | 16 Ga | 0.065" | .37"
3/4" | 16 Ga | 0.065" | .62"
1.0" | 16 Ga | 0.065" | 0.870"
1.5" | 16 Ga | 0.065" | 1.370"
2.0" | 16 Ga | 0.065" | 1.870"
2.5" | 16 Ga | 0.065" | 2.370"
3.0" | 16 Ga | 0.065" | 2.870"
4.0" | 14 Ga | 0.083" | 3.834"
6.0" | 12 Ga | 0.109" | 5.782"
IPS Pipe Size | Gage | Wall Thickness | ID | Gage | Wall Thickness | ID
1.5" | Sch.5 | 0.065" | 1.770"
2.0" | Sch.5 | 0.065" | 2.245"
2.5" | Sch.5 | 0.083" | 2.709"
3.0" | Sch.5 | 0.083" | 3.334"
4.0" | Sch.5 | 0.083" | 4.334"
6.0" | Sch.5 | 0.109" | 6.407"
8.0" | Sch.5 | 0.109" | 8.407" | Sch.10 | 0.148" | 8.329"

## Vlv Press Holding
| WAUKESHA-CHERRY SPECS |  |  |  | CHERRY VALVE SPECS |  |  | PUBLISHED VALUES | [16 empty] | TABLES WITH VALUES INPUT FOR PUBLISHING
[8 empty] | W61 Series Valves AR (Air-to-Raise), Fail Closed (Normally Closed) | [9 empty] | WAUKESHA CHERRY-BURRELL | [6 empty] | W61 Series Valves AR (Air-to-Raise), Fail Closed (Normally Closed)
| Actuator | AR | AL | SPRING | Actuator | Actuator |  |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
| Size (in) | Area (in2) | Area (in2) | FREE LNG | Size (in) | Area (in2) |  |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | HOLDING PRESSURE FOR WAUKESHA CHERRY-BURRELL MODEL W61-T | [8 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
| 4" | 12.12 | 12.12 | 4.25 | 4" | 12.57 |  | Bottom Port (P1), Actuator |  |  | 4" | 160.2143 | 125.2142 | 70.363 | 45.0024 | 31.2414 | 18.1928 | SHUT-OFF VALVES WITH AIR-TO-AIR ACTUATORS | [6 empty] | Bottom Port (P1), Actuator |  | 4" | 160 | 125 | 70 | 45 | 31 | 18
| 5" | 19.19 | 19.19 | 6.22 | 5" | 19.63 |  | Spring holds closed against: |  |  | 5" | 251.094 | 220.1213 | 123.6952 | 79.1124 | 54.9211 | 31.4321 | (ATR PISTON POSITION FOR 6" ACTUATOR) | [6 empty] | Spring holds closed against: |  | 5" | 251 | 220 | 124 | 79 | 55 | 31
| 6" | 27.48 | 27.82 | 6.94 | [6 empty] | 6" | 716.906 | 602.029 | 338.3049 | 216.3715 | 150.2085 | 86.5094 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 1 | PSIG |  |  | 6" | 717 | 602 | 338 | 216 | 150 | 87
[18 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
|  | Effective | Plug Area |  |  |  |  | Side Port (P2), | 50 | psi Air | 4" | 222.855 | 269.5926 | 132.0903 | 79.7583 | 53.7391 | 28.6979 | 4" Actuator | 6.542 | 6.542 | 3.6762 | 2.3512 | 1.6323 | 0.9176 | Side Port (P2), Air to port A, | 50 psi | 4" | 223 | 270 | 132 | 80 | 54 | 29
| Line Size | Upper (in2) | Lower (in2) |  |  | Effective | Plug Area | to air port A, will open against: |  |  | 5" | 356.2971 | 397.6567 | 194.837 | 117.6457 | 79.2667 | 42.7156 | 5" Actuator | 10.3582 | 10.3582 | 5.8207 | 3.7228 | 2.5844 | 1.4529 | will open against: | 50 psi | 5" | 356 | 398 | 195 | 118 | 79 | 43
| 1" | 1.318 | 1.76 |  | Line Size | Upper (in2) | Lower (in2) | NOTE: 75 psi min. for 6" |  |  | 6" | 33.039 | 186.4407 | 91.349 | 55.158 | 37.1641 | 18.1547 | 6" Actuator | 14.833 | 14.833 | 8.3352 | 5.331 | 3.7009 | 2.0805 |  | 75 psi | 6" | 528 | 682 | 334 | 202 | 136 | 72
| 1 1/2" | 1.318 | 1.76 |  | 1 1/2" | 1.318 | 1.76
| 2" | 2.69 | 3.132 |  | 2" | 2.69 | 3.132 | W61 Series Valves AL (Air-to-Lower), Fail Open (Normally Open) | [9 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 10 | PSIG | W61 Series Valves AL (Air-to-Lower), Fail Open (Normally Open)
| 2 1/2" | 4.455 | 4.897 |  | 2 1/2" | 4.455 | 4.897 |  |  |  | Actuator | Valve Size - Pressure in PSI | [5 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" |  |  | Actuator | Valve Size - Pressure in PSI
| 3" | 6.612 | 7.054 |  | 3" | 6.612 | 7.054 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 4" Actuator | 65.4205 | 65.4205 | 36.7625 | 23.5124 | 16.3227 | 9.176 |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
| 4" | 12.106 | 12.548 |  | 4" | 12.106 | 12.548 | Side Port (P2), Actuator Spring |  |  | 4" | 288.4234 | 335.161 | 164.2164 | 99.1565 | 66.8092 | 35.8365 | 5" Actuator | 103.5824 | 103.5824 | 58.2072 | 37.2279 | 25.8442 | 14.5286 | Side Port (P2), Actuator Spring |  | 4" | 288 | 335 | 164 | 99 | 67 | 36
|  | w/ stem | w/o stem |  |  |  |  | Opens Stem Against: |  |  | 5" | 399.8828 | 441.2424 | 216.1924 | 130.5404 | 87.9548 | 47.4609 | 6" Actuator | 148.3295 | 148.3295 | 83.3525 | 53.3102 | 37.0088 | 20.8049 | Opens Stem Against: |  | 5" | 400 | 441 | 216 | 131 | 88 | 47
[11 empty] | 6" | 1065.6087 | 1219.0104 | 597.2698 | 360.641 | 242.9909 | 130.5722 | [9 empty] | 6" | - | - | 597 | 361 | 243 | 131
VALVE SPRING FORCE TABLE | [17 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 20 | PSIG
Valve Type |  | Spring Rate | Pre-load | Pre-load | Stroke | Comp. | Comp. | Lower Port (P1), | 50 | psi Air | 4" | 111.1125 | 76.1124 | 42.7707 | 27.3551 | 18.9903 | 11.3057 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | Lower Port (P1), Air to port B, | 50 psi | 4" | 111 | 76 | 43 | 27 | 19 | 11
|  | Lbs/in | Length | Force (lbs) | Length | Length | Force (lbs) | to air port B, will hold closed against: |  |  | 5" | 218.4542 | 187.4816 | 105.3536 | 67.3816 | 46.7774 | 26.854 | 4" Actuator | 130.8409 | 130.8409 | 73.5249 | 47.0247 | 32.6453 | 18.3519 | will hold closed against: | 50 psi | 5" | 218 | 187 | 105 | 67 | 47 | 27
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | -47.1718 | -162.0487 | -91.0619 | -58.2409 | -40.4318 | -20.6612 | 5" Actuator | 207.1648 | 207.1648 | 116.4144 | 74.4558 | 51.6884 | 29.0572 |  | 75 psi | 6" | 328 | 213 | 120 | 77 | 53 | 32
W61/ 4" AR | 1" | 365 | 3.394 | 296.818 | 0.643 | 2.751 | 519.7782 | [10 empty] | 6" Actuator | 296.6591 | 296.6591 | 166.705 | 106.6204 | 74.0176 | 41.6098 | Consult Factory where line pressures exceed 150 psi.
W61/ 4" AR | 1.5-3" | 365 | 3.581 | 231.9758 | 0.83 | 2.751 | 519.7782 | [17 empty] | Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
W61/ 4" AR | 4" | 365 | 3.557 | 240.2978 | 0.806 | 2.751 | 519.7782 | [10 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 30 | PSIG | 75 psi for 6 inch Actuator
W61/ 4" AL | 1" | 365 | 3.793 | 158.4648 | 0.697 | 3.096 | 400.1495 | W62 Series Valves AR (Air-to-Raise) | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | W62 Series Valves AR (Air-to-Raise)
W61/ 4" AL | 1.5-3" | 365 | 3.793 | 158.4648 | 0.884 | 2.909 | 464.9918 |  |  |  | Actuator | Valve Size - Pressure in PSI | [5 empty] | 4" Actuator | 196.2614 | 196.2614 | 110.2874 | 70.5371 | 48.968 | 27.5279 |  |  | Actuator | Valve Size - Pressure in PSI
W61/ 4" AL | 4" | 365 | 3.793 | 158.4648 | 0.86 | 2.933 | 456.6698 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 5" Actuator | 310.7472 | 310.7472 | 174.6216 | 111.6837 | 77.5326 | 43.5858 |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[8 empty] | Bottom Port (P1), Actuator |  |  | 4" | 125.2142 | 125.2142 | 70.363 | 45.0024 | 31.2414 | 18.6391 | 6" Actuator | 444.9886 | 444.9886 | 250.0575 | 159.9306 | 111.0264 | 62.4147 | Bottom Port (P1), Actuator |  | 4" | 125 | 125 | 70 | 45 | 31 | 19
W61/ 5" AR | 1" | 323 | 4.704 | 465.1846 | 0.631 | 4.073 | 658.807 | Spring holds closed against: |  |  | 5" | 220.1213 | 220.1213 | 123.6952 | 79.1124 | 54.9211 | 31.827 | [7 empty] | Spring holds closed against: |  | 5" | 220 | 220 | 124 | 79 | 55 | 32
W61/ 5" AR | 1.5-3" | 323 | 4.891 | 407.8037 | 0.818 | 4.073 | 658.807 |  |  |  | 6" | 602.029 | 602.029 | 338.3049 | 216.3715 | 150.2085 | 87.9742 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 40 | PSIG |  |  | 6" | 602 | 602 | 338 | 216 | 150 | 88
W61/ 5" AR | 4" | 323 | 4.867 | 415.168 | 0.794 | 4.073 | 658.807 | [10 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W61/ 5" AL | 1" | 323 | 5.116 | 338.7624 | 0.704 | 4.412 | 554.7848 | Middle Side Port (P2), Air to actuator |  |  | 4" | 238.4497 | 253.0487 | 142.1985 | 90.9466 | 63.1366 | 36.5956 | 4" Actuator | 261.6818 | 261.6818 | 147.0498 | 94.0494 | 65.2906 | 36.7039 | Middle Side Port (P2), Air to actuator |  | 4" | 238 | 253 | 142 | 91 | 63 | 37
W61/ 5" AL | 1.5-3" | 323 | 5.116 | 338.7624 | 0.891 | 4.225 | 612.1658 | (with stem raised), spring will |  |  | 5" | 320.327 | 333.2461 | 187.2647 | 119.7699 | 83.1462 | 47.7173 | 5" Actuator | 414.3295 | 414.3295 | 232.8289 | 148.9116 | 103.3768 | 58.1144 | (with stem raised), spring will |  | 5" | 320 | 333 | 187 | 120 | 83 | 48
W61/ 5" AL | 4" | 323 | 5.116 | 338.7624 | 0.867 | 4.249 | 604.8013 | lower against: |  |  | 6" | 973.6898 | 1021.6064 | 574.0828 | 367.1691 | 254.8947 | 146.9109 | 6" Actuator | 593.3182 | 593.3182 | 333.41 | 213.2408 | 148.0352 | 83.2196 | lower against: |  | 6" | - | - | 574 | 367 | 255 | 147
W61/ 6" AR | 1" | 1198 | 5.773 | 1328.1627 | 0.634 | 5.139 | 2049.7181 | Middle Side Port (P2), Air @ |  | 75 | 4" | 487.9917 | 487.9917 | 239.0978 | 144.3711 | 97.2736 | 52.0128 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 50 | PSIG | Middle Side Port (P2), Air to | 50 psi | 4" | 270 | 270 | 132 | 80 | 54 | 28
W61/ 6" AR | 1.5-3" | 1198 | 5.96 | 1115.338 | 0.821 | 5.139 | 2049.7181 | psi to port A,will raise stem (opens)against: |  |  | 5" | 743.4553 | 743.4553 | 364.2654 | 219.9493 | 148.1963 | 79.9539 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | port A, will raise stem | 50 psi | 5" | 398 | 398 | 195 | 118 | 79 | 42
W61/ 6" AR | 4" | 1198 | 5.936 | 1142.6524 | 0.797 | 5.139 | 2049.7181 | NOTE: 75 psi min. for 6" |  |  | 6" | 681.6228 | 681.6228 | 333.9699 | 201.6563 | 135.871 | 70.5477 | 4" Actuator | 327.1023 | 327.1023 | 183.8123 | 117.5618 | 81.6133 | 45.8798 | (opens) against: | 75 psi | 6" | 682 | 682 | 334 | 202 | 136 | 71
W61/ 6" AL | 1" | 1198 | 6.242 | 794.3938 | 0.601 | 5.641 | 1478.3919 | [10 empty] | 5" Actuator | 517.9119 | 517.9119 | 291.0361 | 186.1395 | 129.221 | 72.6431
W61/ 6" AL | 1.5-3" | 1198 | 6.242 | 794.3938 | 0.788 | 5.454 | 1691.2166 | Upper Side Port (P3), Air @ |  | 75 | 4" | 336.7818 | 317.287 | 155.4588 | 93.8685 | 63.2463 | 33.4007 | 6" Actuator | 741.6477 | 741.6477 | 416.7625 | 266.5509 | 185.0439 | 104.0245 | Upper Side Port (P3), Air to | 50 psi | 4" | 118 | 99 | 48 | 29 | 20 | 10
W61/ 6" AL | 4" | 1198 | 6.242 | 794.3938 | 0.764 | 5.478 | 1663.9022 | to Port A, w/stem raised,will hold against: |  |  | 5" | 609.6449 | 592.3933 | 290.2507 | 175.258 | 118.0845 | 63.4835 | [7 empty] | port A, (with stem raised), | 50 psi | 5" | 264 | 247 | 121 | 73 | 49 | 26
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | 185.3232 | 121.3374 | 59.4508 | 35.8974 | 24.1867 | 9.4592 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 60 | PSIG | will hold against: | 75 psi | 6" | 185 | 121 | 59 | 36 | 24 | 9
W62/ 4" AR | 1" | 365 | 3.581 | 231.9758 | 0.605 | 2.976 | 441.7595 | [10 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | Consult Factory where line pressures exceed 150 psi.
W62/ 4" AR | 1.5-3" | 365 | 3.581 | 231.9758 | 0.683 | 2.898 | 468.806 | [10 empty] | 4" Actuator | 392.5227 | 392.5227 | 220.5747 | 141.0741 | 97.9359 | 55.0558 | Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
W62/ 4" AR | 4" | 365 | 3.54 | 246.1925 | 0.684 | 2.856 | 483.3695 | [10 empty] | 5" Actuator | 621.4943 | 621.4943 | 349.2433 | 223.3674 | 155.0652 | 87.1717 | 75 psi for 6 inch Actuator
W62/ 4" AL | 1" | 365 | 3.514 | 255.208 | 0.605 | 2.909 | 464.9918 | W62 Series Valves AL (Air-to-Lower) | [9 empty] | 6" Actuator | 889.9773 | 889.9773 | 500.1149 | 319.8611 | 222.0527 | 124.8295 | W62 Series Valves AL (Air-to-Lower)
W62/ 4" AL | 1.5-3" | 365 | 3.592 | 228.1615 | 0.683 | 2.909 | 464.9918 |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
W62/ 4" AL | 4" | 323 | 3.634 | 189.0196 | 0.684 | 2.95 | 398.905 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 70 | PSIG |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[8 empty] | Bottom Port (P1), Air @ |  | 75 | 4" | 239.6635 | 239.6635 | 134.6768 | 86.136 | 59.797 | 38.6189 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | Bottom Port (P1), Air to | 50 psi | 4" | 76 | 76 | 43 | 27 | 19 | 16
W62/ 5" AR | 1" | 323 | 4.891 | 407.8037 | 0.605 | 4.286 | 593.4479 | Psi, Air to Port B, will hold against: |  |  | 5" | 446.4375 | 446.4375 | 250.8717 | 160.4513 | 111.3879 | 63.5704 | 4" Actuator | 457.9432 | 457.9432 | 257.3372 | 164.5865 | 114.2586 | 64.2318 | port B, will hold against: | 50 psi | 5" | 187 | 187 | 105 | 67 | 47 | 27
W62/ 5" AR | 1.5-3" | 323 | 4.891 | 407.8037 | 0.683 | 4.208 | 617.3822 | NOTE: 75 psi min. for 6" |  |  | 6" | 213.3632 | 213.3632 | 119.8976 | 76.6835 | 53.2349 | 33.4594 | 5" Actuator | 725.0767 | 725.0767 | 407.4505 | 260.5953 | 180.9094 | 101.7003 |  | 75 psi | 6" | 213 | 213 | 120 | 77 | 53 | 33
W62/ 5" AR | 4" | 323 | 4.85 | 420.3845 | 0.684 | 4.166 | 630.2699 | [10 empty] | 6" Actuator | 1038.3068 | 1038.3068 | 583.4674 | 373.1713 | 259.0615 | 145.6344
W62/ 5" AL | 1" | 323 | 4.83 | 426.5215 | 0.605 | 4.225 | 612.1658 | Middle Port (P2), (stem lowered), spring |  |  | 4" | 335.161 | 335.161 | 164.2164 | 99.1565 | 66.8092 | 31.3035 | [7 empty] | Middle Port (P2), (stem lowered), spring |  | 4" | 335 | 335 | 164 | 99 | 67 | 31
W62/ 5" AL | 1.5-3" | 323 | 4.908 | 402.5872 | 0.683 | 4.225 | 612.1658 | opens stem against: |  |  | 5" | 441.2424 | 441.2424 | 216.1924 | 130.5404 | 87.9548 | 47.0515 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 75 | PSIG | opens stem against: |  | 5" | 441 | 441 | 216 | 131 | 88 | 47
W62/ 5" AL | 4" | 323 | 4.95 | 389.6995 | 0.684 | 4.266 | 599.5849 |  |  |  | 6" | 1219.0104 | 1219.0104 | 597.2698 | 360.641 | 242.9909 | 129.0539 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" |  |  | 6" | - | - | 597 | 361 | 243 | 129
[18 empty] | 4" Actuator | 490.6534 | 490.6534 | 275.7184 | 176.3427 | 122.4199 | 68.8197
W62/ 6" AR | 1" | 1198 | 5.96 | 1115.338 | 0.605 | 5.355 | 1803.8885 | Middle Side Port (P2), Air @ |  | 75 | 4" | 352.8991 | 367.4981 | 206.5123 | 132.0802 | 91.6922 | 54.5092 | 5" Actuator | 776.8679 | 776.8679 | 436.5541 | 279.2092 | 193.8315 | 108.9646 | Middle Side Port (P2), Air to | 50 psi | 4" | 189 | 204 | 115 | 73 | 51 | 32
W62/ 6" AR | 1.5-3" | 1198 | 5.96 | 1115.338 | 0.683 | 5.277 | 1892.6603 | to port B, (w/stem raised), |  |  | 5" | 546.6432 | 559.5623 | 314.4411 | 201.1088 | 139.6129 | 79.4607 | 6" Actuator | 1112.4716 | 1112.4716 | 625.1437 | 399.8264 | 277.5659 | 156.0368 | port B, (w/stem raised), will | 50 psi | 5" | 288 | 301 | 169 | 108 | 75 | 43
W62/ 6" AR | 4" | 1198 | 5.919 | 1162.0001 | 0.684 | 5.235 | 1940.4605 | will close stem against: |  |  | 6" | 585.024 | 632.9406 | 355.6754 | 227.4812 | 157.9211 | 92.396 | [7 empty] | close stem against: | 75 psi | 6" | 585 | 633 | 356 | 227 | 158 | 92
W62/ 6" AL | 1" | 1198 | 6.059 | 1002.6661 | 0.605 | 5.454 | 1691.2166 | NOTE: 75 psi min. for 6"
W62/ 6" AL | 1.5-3" | 1198 | 6.137 | 913.8943 | 0.683 | 5.454 | 1691.2166 | Upper Side Port (P3), (stem raised) |  |  | 4" | 183.9511 | 164.4563 | 80.5775 | 48.654 | 32.7818 | 14.833 | [7 empty] | Upper Side Port (P3), (stem raised) |  | 4" | 184 | 164 | 81 | 49 | 33 | 15
W62/ 6" AL | 4" | 1198 | 6.179 | 866.0941 | 0.684 | 5.495 | 1644.5545 | Actuator spring holds against: |  |  | 5" | 307.432 | 290.1805 | 142.1776 | 85.8491 | 57.843 | 30.5811 | [7 empty] | Actuator spring holds against: |  | 5" | 307 | 290 | 142 | 86 | 58 | 31
[11 empty] | 6" | 722.7108 | 658.725 | 322.7508 | 194.8821 | 131.3067 | 67.9654 | [9 empty] | 6" | 723 | 659 | 323 | 195 | 131 | 68
W63/ 4" AR | 1" | 365 | 3.793 | 158.4648 | 0.63 | 3.163 | 376.9173 | [17 empty] | Consult Factory where line pressures exceed 150 psi.
W63/ 4" AR | 1.5-3" | 365 | 3.793 | 158.4648 | 0.895 | 2.898 | 468.806 | [17 empty] | Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
W63/ 4" AR | 4" | 365 | 3.793 | 158.4648 | 0.937 | 2.856 | 483.3695 | [17 empty] | 75 psi for 6 inch Actuator
W63/ 4" AL | 1" | 365 | 3.327 | 320.0503 | 0.576 | 2.751 | 519.7782
W63/ 4" AL | 1.5-3" | 365 | 3.592 | 228.1615 | 0.841 | 2.751 | 519.7782 | W63 Series Valves AR (Air-to-Raise), Fail Open (Normally Open) | [16 empty] | W63 Series Valves AR (Air-to-Raise), Fail Open (Normally Open)
W63/ 4" AL | 4" | 365 | 3.634 | 213.598 | 0.883 | 2.751 | 519.7782 |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W63/ 5" AR | 1" | 323 | 5.116 | 338.7624 | 0.643 | 4.473 | 536.067 | Bottom Port (P2), stem raised, |  |  | 4" | 203.4497 | 253.0487 | 142.1985 | 90.9466 | 63.1366 | 36.5956 | [7 empty] | Bottom Port (P2), stem raised, |  | 4" | 203 | 253 | 142 | 91 | 63 | 37
W63/ 5" AR | 1.5-3" | 323 | 5.116 | 338.7624 | 0.908 | 4.208 | 617.3822 | Actuator spring will open against: |  |  | 5" | 289.3543 | 333.2461 | 187.2647 | 119.7699 | 83.1462 | 47.7173 | [7 empty] | Actuator spring will open against: |  | 5" | 289 | 333 | 187 | 120 | 83 | 48
W63/ 5" AR | 4" | 323 | 5.116 | 338.7624 | 0.95 | 4.166 | 630.2699 |  |  |  | 6" | 858.8128 | 1021.6064 | 574.0828 | 367.1691 | 254.8947 | 146.9109 | [9 empty] | 6" | - | - | 574 | 367 | 255 | 147
W63/ 5" AL | 1" | 323 | 4.643 | 483.9024 | 0.57 | 4.073 | 658.807
W63/ 5" AL | 1.5-3" | 323 | 4.908 | 402.5872 | 0.835 | 4.073 | 658.807 | Top Port (P1), | 75 | psi Air to | 4" | 383.5194 | 317.287 | 155.4588 | 93.8685 | 63.2463 | 33.4007 | [7 empty] | Top Port (P1), Air to | 50 psi | 4" | 165 | 99 | 48 | 29 | 20 | 10
W63/ 5" AL | 4" | 323 | 4.95 | 389.6995 | 0.877 | 4.073 | 658.807 | port A, will hold valve closed against: |  |  | 5" | 651.0045 | 592.3933 | 290.2507 | 175.258 | 118.0845 | 63.4835 | [7 empty] | port A, will hold valve | 50 psi | 5" | 305 | 247 | 121 | 73 | 49 | 26
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | 338.7249 | 121.3374 | 59.4508 | 35.8974 | 24.1867 | 9.4592 | [7 empty] | closed against: | 75 psi | 6" | 339 | 121 | 59 | 36 | 24 | 9
W63/ 6" AR | 1" | 1198 | 6.242 | 794.3938 | 0.7 | 5.542 | 1591.0638
W63/ 6" AR | 1.5-3" | 1198 | 6.242 | 794.3938 | 0.965 | 5.277 | 1892.6603 | W63 Series Valves AL (Air-to-Lower), Fail Closed (Normally Closed) | [16 empty] | W63 Series Valves AL (Air-to-Lower), Fail Closed (Normally Closed)
W63/ 6" AR | 4" | 1198 | 6.242 | 794.3938 | 1.007 | 5.235 | 1940.4605 |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
W63/ 6" AL | 1" | 1198 | 5.872 | 1215.4908 | 0.733 | 5.139 | 2049.7181 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W63/ 6" AL | 1.5-3" | 1198 | 6.137 | 913.8943 | 0.998 | 5.139 | 2049.7181 | Top Port (P1), Actuator Spring |  |  | 4" | 230.6887 | 164.4563 | 80.5775 | 48.654 | 32.7818 | 16.7618 | [7 empty] | Top Port (P1), Actuator Spring |  | 4" | 231 | 164 | 81 | 49 | 33 | 17
W63/ 6" AL | 4" | 1198 | 6.179 | 866.0941 | 1.04 | 5.139 | 2049.7181 | Holds Closed Against: |  |  | 5" | 348.7916 | 290.1805 | 142.1776 | 85.8491 | 57.843 | 30.5811 | [7 empty] | Holds Closed Against: |  | 5" | 349 | 290 | 142 | 86 | 58 | 31
[11 empty] | 6" | 876.1125 | 658.725 | 322.7508 | 194.8821 | 131.3067 | 67.9654 | [9 empty] | 6" | - | 659 | 323 | 195 | 131 | 68
W65/ 4" AR | 1" | 365 | 3.393 | 297.1648 | 0.519 | 2.874 | 477.128
W65/ 4" AR | 1.5" | 365 | 3.603 | 224.3473 | 0.649 | 2.954 | 449.388 | Lower Port (P2), | 75 | psi Air | 4" | 317.899 | 367.4981 | 206.5123 | 132.0802 | 91.6922 | 52.6484 | [7 empty] | Lower Port (P2), Air to | 50 psi | 4" | 154 | 204 | 115 | 73 | 51 | 30
W65/ 4" AR | 2" | 365 | 3.631 | 214.6382 | 0.736 | 2.895 | 469.8462 | to port B, will open stem against: |  |  | 5" | 515.6706 | 559.5623 | 314.4411 | 201.1088 | 139.6129 | 79.4607 | [7 empty] | port B, will open against: | 50 psi | 5" | 257 | 301 | 169 | 108 | 75 | 43
W65/ 4" AR | 2.5" | 365 | 3.575 | 234.0563 | 0.679 | 2.896 | 469.4995 | NOTE: 75 psi min. for 6" |  |  | 6" | 470.147 | 632.9406 | 355.6754 | 227.4812 | 157.9211 | 92.396 | [8 empty] | 75 psi | 6" | 470 | 633 | 356 | 227 | 158 | 92
W65/ 4" AR | 3" | 365 | 3.574 | 234.403 | 0.691 | 2.883 | 474.0072 | [17 empty] | Consult Factory where line pressures exceed 150 psi.
W65/ 4" AR | 4" | 365 | 3.563 | 238.2173 | 0.703 | 2.86 | 481.9825 | [17 empty] | Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
W65/ 4" AL | 1" | 365 | 3.616 | 219.8395 | 0.519 | 3.097 | 399.8028 | [17 empty] | 75 psi for 6 inch Actuator
W65/ 4" AL | 1.5" | 365 | 3.536 | 247.5795 | 0.649 | 2.887 | 472.6202 | W65 Series Valves AR (Air-to-Raise) | [16 empty] | W65 Series Valves AR (Air-to-Raise)
W65/ 4" AL | 2" | 365 | 3.595 | 227.1213 | 0.736 | 2.859 | 482.3293 |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
W65/ 4" AL | 2.5" | 365 | 3.594 | 227.468 | 0.679 | 2.915 | 462.9112 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W65/ 4" AL | 3" | 365 | 3.607 | 222.9603 | 0.686 | 2.921 | 460.8308 | Middle Port (P1), Actuator |  |  | 4" | 214.1931 | 161.707 | 75.8016 | 49.911 | 33.6786 | 18.6937 | [7 empty] | Middle Port (P1), Actuator |  | 4" | 214 | 162 | 76 | 50 | 34 | 19
W65/ 4" AL | 4" | 365 | 3.63 | 214.985 | 0.703 | 2.927 | 458.7502 | Spring holds closed against: |  |  | 5" | 335.5212 | 289.0746 | 138.6015 | 87.3541 | 58.9011 | 32.4352 | [7 empty] | Spring holds closed against: |  | 5" | 336 | 289 | 139 | 87 | 59 | 32
[11 empty] | 6" | 958.1455 | 785.8762 | 366.5613 | 239.2948 | 161.3944 | 89.1321 | [9 empty] | 6" | - | 786 | 367 | 239 | 161 | 89
W65/ 5" AR | 1" | 323 | 4.703 | 465.4914 | 0.519 | 4.184 | 624.7466
W65/ 5" AR | 1.5" | 323 | 4.913 | 401.053 | 0.649 | 4.264 | 600.1986 | Lower Port (P3), Stem Raised |  |  | 4" | 343.9086 | 343.9086 | 168.5025 | 101.7445 | 68.5529 | 37.4419 | [7 empty] | Lower Port (P3), Stem Raised |  | 4" | 344 | 344 | 169 | 102 | 69 | 37
W65/ 5" AR | 2" | 323 | 4.941 | 392.4611 | 0.736 | 4.205 | 618.3027 | Spring lowers stem against: |  |  | 5" | 450.3105 | 432.6166 | 218.3597 | 131.8491 | 89.3657 | 49.3632 | [7 empty] | Spring lowers stem against: |  | 5" | 450 | 433 | 218 | 132 | 89 | 49
W65/ 5" AR | 2.5" | 323 | 4.885 | 409.6447 | 0.68 | 4.205 | 618.3027 |  |  |  | 6" | 1383.8968 | 1318.2704 | 669.6174 | 404.083 | 274.3868 | 151.9175 | [9 empty] | 6" | - | - | 670 | 404 | 274 | 152
W65/ 5" AR | 3" | 323 | 4.884 | 409.9516 | 0.691 | 4.193 | 621.985
W65/ 5" AR | 4" | 323 | 4.873 | 413.327 | 0.703 | 4.17 | 629.0425 | Top Port (P2), Air @ psi |  | 35 | 4" | 91.5656 | 144.0517 | 74.0088 | 40.5469 | 27.2697 | 14.5947 | [7 empty] | Top Port (P2), Air to | 50 psi | 4" | 223 | 275 | 138 | 79 | 53 | 29
W65/ 5" AL | 1" | 323 | 4.932 | 395.2228 | 0.519 | 4.413 | 554.4779 | to port A, will raise stem against: |  |  | 5" | 148.5968 | 195.0434 | 98.5983 | 55.8709 | 37.6003 | 20.2715 | [7 empty] | port A, will raise | 50 psi | 5" | 356 | 403 | 200 | 117 | 79 | 43
W65/ 5" AL | 1.5" | 323 | 4.852 | 419.7708 | 0.649 | 4.203 | 618.9165 | NOTE: 75 psi min. for 6" |  |  | 6" | -264.8906 | -92.6213 | -26.8921 | -34.1971 | -23.2047 | -13.6563 | [7 empty] | stem against: | 75 psi | 6" | 527 | 700 | 361 | 200 | 135 | 73
W65/ 5" AL | 2" | 323 | 4.911 | 401.6667 | 0.736 | 4.175 | 627.5082
W65/ 5" AL | 2.5" | 323 | 4.91 | 401.9735 | 0.679 | 4.231 | 610.3247 | Middle Port (P1), Air @ |  | 75 | 4" | 311.2886 | 331.2833 | 155.0915 | 93.7206 | 62.499 | 33.5096 | [7 empty] | Middle Port (P1), Air to | 50 psi | 4" | 93 | 113 | 48 | 29 | 19 | 10
W65/ 5" AL | 3" | 323 | 4.923 | 397.9844 | 0.686 | 4.237 | 608.4836 | to port A,(w/stem raised), will hold against: |  |  | 5" | 587.0852 | 604.7791 | 289.9256 | 175.0617 | 117.4231 | 63.5798 | [7 empty] | port A (with stem raised), | 50 psi | 5" | 241 | 259 | 120 | 73 | 48 | 26
W65/ 5" AL | 4" | 323 | 4.946 | 390.9269 | 0.703 | 4.243 | 606.6425 | NOTE: 75 psi min. for 6" |  |  | 6" | 101.6495 | 167.2759 | 58.245 | 35.412 | 21.7339 | 9.8164 | [7 empty] | will hold against: | 75 psi | 6" | 102 | 167 | 58 | 35 | 22 | 10
Consult Factory where line pressures exceed 150 psi.
W65/ 6" AR | 1" | 1198 | 5.772 | 1329.3008 | 0.519 | 5.253 | 1919.9747 | [17 empty] | Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
W65/ 6" AR | 1.5" | 1198 | 5.982 | 1090.2998 | 0.649 | 5.333 | 1828.9267 | [17 empty] | 75 psi for 6 inch Actuator
W65/ 6" AR | 2" | 1198 | 6.028 | 1037.9472 | 0.754 | 5.274 | 1896.0746 | W65 Series Valves AL (Air-to-Lower) | [16 empty] | W65 Series Valves AL (Air-to-Lower)
W65/ 6" AR | 2.5" | 1198 | 5.954 | 1122.1666 | 0.679 | 5.275 | 1894.9365 |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
W65/ 6" AR | 3" | 1198 | 5.953 | 1123.3047 | 0.691 | 5.262 | 1909.7318 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W65/ 6" AR | 4" | 1198 | 5.942 | 1135.8238 | 0.703 | 5.239 | 1935.9081 | Middle Port (P1), Air @ |  | 50 | 4" | 148.6247 | 96.1387 | 43.6755 | 30.5128 | 20.8577 | 11.5552 | [7 empty] | Middle Port (P1), Air to | 50 psi | 4" | 149 | 96 | 44 | 31 | 21 | 12
W65/ 6" AL | 1" | 1198 | 6.161 | 886.5799 | 0.519 | 5.642 | 1477.2538 | to port B, will hold closed against: |  |  | 5" | 291.9355 | 245.4889 | 117.2462 | 74.4594 | 50.4334 | 27.69 | [7 empty] | port B, will hold | 50 psi | 5" | 292 | 245 | 117 | 74 | 50 | 28
W65/ 6" AL | 1.5" | 1198 | 6.081 | 977.6279 | 0.649 | 5.432 | 1716.2548 | NOTE: 75 psi min. for 6" |  |  | 6" | -62.1708 | -234.4401 | -126.121 | -62.5631 | -41.1723 | -21.9515 | [7 empty] | closed against: | 75 psi | 6" | 439 | 267 | 120 | 86 | 59 | 33
W65/ 6" AL | 2" | 1198 | 6.14 | 910.48 | 0.736 | 5.404 | 1748.1216
W65/ 6" AL | 2.5" | 1198 | 6.134 | 917.3086 | 0.674 | 5.46 | 1684.388 | Middle Port (P1), (stem raised), spring |  |  | 4" | 158.4579 | 178.4526 | 80.2101 | 48.5061 | 32.0345 | 16.8706 | [7 empty] | Middle Port (P1), (stem raised), spring |  | 4" | 158 | 178 | 80 | 49 | 32 | 17
W65/ 6" AL | 3" | 1198 | 6.152 | 896.8228 | 0.686 | 5.466 | 1677.5594 | holds closed against: |  |  | 5" | 284.8723 | 302.5662 | 141.8525 | 85.7183 | 57.1817 | 30.6774 | [7 empty] | holds closed against: |  | 5" | 285 | 303 | 142 | 86 | 57 | 31
W65/ 6" AL | 4" | 1198 | 6.175 | 870.6465 | 0.703 | 5.472 | 1670.7308 |  |  |  | 6" | 639.0371 | 704.6635 | 321.545 | 195.6101 | 128.8539 | 68.3227 | [9 empty] | 6" | 639 | 705 | 322 | 196 | 129 | 68
[8 empty] | Lower Port (P3), Air @ psi |  | 50 | 4" | 278.3403 | 258.3456 | 133.8048 | 80.7195 | 55.0344 | 30.6843 | [7 empty] | Lower Port (P3), Air | 50 psi | 4" | 278 | 258 | 134 | 81 | 55 | 31
[8 empty] | to port B, will lower stem against: |  |  | 5" | 406.7248 | 389.0309 | 197.0043 | 118.8889 | 80.6775 | 44.6179 | [7 empty] | to port B, will lower | 50 psi | 5" | 407 | 389 | 197 | 119 | 81 | 45
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | 363.5805 | 297.9541 | 169.7004 | 101.0116 | 71.0025 | 40.834 | [7 empty] | stem against: | 75 psi | 6" | - | - | 415 | 249 | 171 | 95
[8 empty] | Upper Port (P2), stem lowered, |  |  | 4" | 288.1735 | 340.6595 | 170.3393 | 98.7128 | 66.2113 | 35.9997 | [7 empty] | Upper Port (P2), stem lowered, |  | 4" | 288 | 341 | 170 | 99 | 66 | 36
[8 empty] | Actuator spring raises stem against: |  |  | 5" | 399.6616 | 446.1082 | 221.6107 | 130.1478 | 87.4258 | 47.6053 | [7 empty] | Actuator spring raises stem against: |  | 5" | 400 | 446 | 222 | 130 | 87 | 48
| WAUKESHA-CHERRY SPECS |  |  |  | CHERRY VALVE SPECS | [5 empty] | 6" | 1064.7884 | 1237.0577 | 617.3664 | 359.1849 | 241.0286 | 131.1081 | [9 empty] | 6" | - | - | 617 | 359 | 241 | 131
| Effective Plug Diameter |  |  |  | Effective Plug Diameter | [19 empty] | Consult Factory where line pressures exceed 150 psi.
| Line Size | Upper (in) | Lower (in) |  | Line Size | Upper (in) | Lower (in) | [17 empty] | Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
| 1" | 1.2954 | 1.497 |  | 1 1/2" | 1.2954 | 1.497 | [17 empty] | 75 psi for 6 inch Actuator
| 1 1/2" | 1.2954 | 1.497 |  | 2" | 1.8507 | 1.9969 | W64R Series Valves AR (Air-to-Raise), Fail Closed (Normally Closed) | [16 empty] | W64R Series Valves AR (Air-to-Raise), Fail Closed (Normally Closed)
| 2" | 1.8507 | 1.9969 |  | 2 1/2" | 2.3817 | 2.497 |  |  |  | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
| 2 1/2" | 2.3817 | 2.497 |  | 3" | 2.9015 | 2.9969 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
| 3" | 2.9015 | 2.9969 |  | 4" | 3.926 | 3.9971 | Tank Port (P1), Actuator |  |  | 4" | 160.2143 | 125.2142 | 70.363 | 45.0024 | 31.2414 | 18.1928 | [7 empty] | Tank Port (P1), Actuator |  | 4" | 160 | 125 | 70 | 45 | 31 | 18
| 4" | 3.926 | 3.9971 |  |  | w/ stem | w/o stem | Spring holds closed against: |  |  | 5" | 251.094 | 220.1213 | 123.6952 | 79.1124 | 54.9211 | 31.4321 | [7 empty] | Spring holds closed against: |  | 5" | 251 | 220 | 124 | 79 | 55 | 31
|  | w/ stem | w/o stem | [7 empty] | 6" | 716.906 | 602.029 | 338.3049 | 216.3715 | 150.2085 | 86.5094 | [9 empty] | 6" | 717 | 602 | 338 | 216 | 150 | 87
| Actuator | AR | AL | SPRING |  | VOLUME |  | Side Port (P2), | 50 | psi Air | 4" | 222.855 | 269.5926 | 132.0903 | 79.7583 | 53.7391 | 28.6979 | [7 empty] | Side Port (P2), Air | 50 psi | 4" | 223 | 270 | 132 | 80 | 54 | 29
| Size (in) | Area (in2) | Area (in2) | FREE LNG | RATE | AR | AL | to port A, will open against: |  |  | 5" | 356.2971 | 397.6567 | 194.837 | 117.6457 | 79.2667 | 42.7156 | [7 empty] | to port A, will open against: | 50 psi | 5" | 356 | 398 | 195 | 118 | 79 | 43
| 4" | 12.12 | 12.12 | 4.25 | 365 | 12.7 | 14 | NOTE: 75 psi min. for 6" |  |  | 6" | 33.039 | 186.4407 | 91.349 | 55.158 | 37.1641 | 18.1547 | [8 empty] | 75 psi | 6" | 528 | 682 | 334 | 202 | 136 | 72
| 5" | 19.19 | 19.19 | 6.22 | 323 | 21.5 | 27.1
| 6" | 27.48 | 27.82 | 6.94 | 1198 | 31.2 | 33.1 | W64R Series Valves AL (Air-to-Lower), Fail Open (Normally Open) | [16 empty] | W64R Series Valves AL (Air-to-Lower), Fail Open (Normally Open)
[11 empty] | Actuator | Valve Size - Pressure in PSI | [14 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[8 empty] | Side Port (P2), Actuator Spring |  |  | 4" | 288.4234 | 335.161 | 164.2164 | 99.1565 | 66.8092 | 35.8365 | [7 empty] | Side Port (P2), Actuator Spring |  | 4" | 288 | 335 | 164 | 99 | 67 | 36
[8 empty] | Opens Stem Against: |  |  | 5" | 399.8828 | 441.2424 | 216.1924 | 130.5404 | 87.9548 | 47.4609 | [7 empty] | Opens Stem Against: |  | 5" | 400 | 441 | 216 | 131 | 88 | 47
[11 empty] | 6" | 1065.6087 | 1219.0104 | 597.2698 | 360.641 | 242.9909 | 130.5722 | [9 empty] | 6" | - | - | 597 | 361 | 243 | 131
[8 empty] | Tank Port (P1), | 75 | psi Air | 4" | 274.6636 | 239.6635 | 134.6768 | 86.136 | 59.797 | 34.2456 | [7 empty] | Tank Port (P1), Air to | 50 psi | 4" | 111 | 76 | 43 | 27 | 19 | 11
[8 empty] | to port B, will hold closed against: |  |  | 5" | 477.4102 | 446.4375 | 250.8717 | 160.4513 | 111.3879 | 63.1755 | [7 empty] | port B, will hold | 50 psi | 5" | 218 | 187 | 105 | 67 | 47 | 27
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | 328.2402 | 213.3632 | 119.8976 | 76.6835 | 53.2349 | 31.9946 | [7 empty] | closed against: | 75 psi | 6" | 328 | 213 | 120 | 77 | 53 | 32
Consult Factory where line pressures exceed 150 psi.
Normal Air Requirement: 50 psi for 4 and 5 inch Actuator
[8 empty] | W64 Series Valves AR (Air-to-Raise), Fail Open (Normally Open) | [16 empty] | 75 psi for 6 inch Actuator
[11 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [7 empty] | W64 Series Valves AR (Air-to-Raise), Fail Open (Normally Open)
[8 empty] | Tank Port (P1), stem raised, |  |  | 4" | 203.4497 | 253.0487 | 142.1985 | 90.9466 | 63.1366 | 36.5956 | [9 empty] | Actuator | Valve Size - Pressure in PSI
[8 empty] | Actuator spring will open against: |  |  | 5" | 289.3543 | 333.2461 | 187.2647 | 119.7699 | 83.1462 | 47.7173 | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[11 empty] | 6" | 858.8128 | 1021.6064 | 574.0828 | 367.1691 | 254.8947 | 146.9109 | [7 empty] | Tank Port (P1), stem raised, |  | 4" | 203 | 253 | 142 | 91 | 63 | 37
[25 empty] | Actuator spring will open against: |  | 5" | 289 | 333 | 187 | 120 | 83 | 48
[8 empty] | Side Port (P2), | 50 | psi Air | 4" | 165.1203 | 98.8879 | 48.4514 | 29.2557 | 19.7118 | 9.6232 | [9 empty] | 6" | - | - | 574 | 367 | 255 | 147
[8 empty] | to port A, will hold valve closed against: |  |  | 5" | 305.2059 | 246.5948 | 120.8223 | 72.9544 | 49.1549 | 25.8358
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | -156.4572 | -373.8447 | -183.17 | -110.601 | -74.5202 | -44.4521 | [7 empty] | Side Port (P2), Air to port A | 50 psi | 4" | 165 | 99 | 48 | 29 | 20 | 10
[25 empty] | will hold valve closed against: | 50 psi | 5" | 305 | 247 | 121 | 73 | 49 | 26
[8 empty] | W64 Series Valves AL (Air-to-Lower), Fail Closed (Normally Closed) | [17 empty] | 75 psi | 6" | 339 | 121 | 59 | 36 | 24 | 9
[11 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | [7 empty] | W64 Series Valves AL (Air-to-Lower), Fail Closed (Normally Closed)
[8 empty] | Side Port (P2), Actuator Spring |  |  | 4" | 230.6887 | 164.4563 | 80.5775 | 48.654 | 32.7818 | 16.7618 | [9 empty] | Actuator | Valve Size - Pressure in PSI
[8 empty] | Holds Closed Against: |  |  | 5" | 348.7916 | 290.1805 | 142.1776 | 85.8491 | 57.843 | 30.5811 | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[11 empty] | 6" | 876.1125 | 658.725 | 322.7508 | 194.8821 | 131.3067 | 67.9654 | [7 empty] | Side Port (P2), Actuator Spring |  | 4" | 231 | 164 | 81 | 49 | 33 | 17
[25 empty] | Holds Closed Against: |  | 5" | 349 | 290 | 142 | 86 | 58 | 31
[8 empty] | Tank Port (P1), | 50 | psi Air | 4" | 154.3479 | 203.9469 | 114.6062 | 73.2993 | 50.8855 | 29.7085 | [9 empty] | 6" | - | 659 | 323 | 195 | 131 | 68
[8 empty] | to port B, will open stem against: |  |  | 5" | 256.7146 | 300.6063 | 168.9231 | 108.039 | 75.0024 | 43.1392
[8 empty] | NOTE: 75 psi min. for 6" |  |  | 6" | 94.7351 | 257.5286 | 144.716 | 92.5568 | 64.2544 | 39.7402 | [7 empty] | Tank Port (P1), Air to port B | 50 psi | 4" | 154 | 204 | 115 | 73 | 51 | 30
[25 empty] | will open stem against: | 50 psi | 5" | 257 | 301 | 169 | 108 | 75 | 43
[26 empty] | 75 psi | 6" | 470 | 633 | 356 | 227 | 158 | 92

## Cv DPress valves
ΔP= Q2(SG)/Cv2
3" W65 (S-T Flow Either way)
Cv= | 2.9
Flow (Q) gpm
| 60 | 240
SG | 1 | 1
ΔP (psid) | 10 | 6848.9893 | 23.1
x (2) Valves | 20 | 13697.9786

## Vlv Press Holding- LONG STROKE
| WAUKESHA-CHERRY SPECS Long Stroke Actuators | [6 empty] | LONG STROKE SPRING VALUES | [9 empty] | AIR TO AIR ACTUATOR
[8 empty] | W61 Series Valves AR (Air-to-Raise), Fail Closed (Normally Closed) | [9 empty] | WAUKESHA CHERRY-BURRELL
| Actuator | AR | AL | SPRING | [6 empty] | Actuator | Valve Size - Pressure in PSI
| Size (in) | Area (in2) | Area (in2) | FREE LNG | [6 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | HOLDING PRESSURE FOR WAUKESHA CHERRY-BURRELL MODEL W61-T
| 4" | 12.12 | 12.12 | 12.5 |  |  |  | Bottom Port (P1), Actuator |  |  | 4LS" | 91.455 | 91.455 | 51.3924 | 32.8693 | 22.8184 | 12.9139 | SHUT-OFF VALVES WITH AIR-TO-AIR ACTUATORS
| 5" | 19.19 | 19.19 | 6.22 |  |  |  | Spring holds closed against: |  |  |  | 251.094 | 220.1213 | 123.6952 | 79.1124 | 54.9211 | 31.4321 | (ATR PISTON POSITION FOR 6" ACTUATOR)
| 6" | 27.48 | 27.82 | 19.14 | [6 empty] | 6LS" | 311.9625 | 321.2951 | 180.549 | 112.1205 | 80.1644 | 43.9023 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 1 | PSIG
[18 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
|  | Effective | Plug Area |  |  |  |  | Side Port (P2), | 50 | psi Air | 4LS" | 314.6731 | 314.6731 | 154.1781 | 93.0952 | 62.7252 | 34.1695 | 4" Actuator | 6.542 | 6.542 | 3.6762 | 2.3512 | 1.6323 | 0.9176
| Line Size | Upper (in2) | Lower (in2) |  |  | Effective | Plug Area | to air port A, will open against: |  |  | - | 356.2971 | 397.6567 | 194.837 | 117.6457 | 79.2667 | 42.7156 | 5" Actuator | 10.3582 | 10.3582 | 5.8207 | 3.7228 | 2.5844 | 1.4529
| 1" | 1.318 | 1.76 |  | Line Size | Upper (in2) | Lower (in2) |  |  |  | 6LS" | 573.7831 | 561.3206 | 275.0262 | 169.7522 | 111.8906 | 62.3174 | 6" Actuator | 14.833 | 14.833 | 8.3352 | 5.331 | 3.7009 | 2.0805
| 1 1/2" | 1.318 | 1.76 |  | 1 1/2" | 1.318 | 1.76
| 2" | 2.69 | 3.132 |  | 2" | 2.69 | 3.132 | W61 Series Valves AL (Air-to-Lower), Fail Open (Normally Open) | [9 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 10 | PSIG
| 2 1/2" | 4.455 | 4.897 |  | 2 1/2" | 4.455 | 4.897 |  |  |  | Actuator | Valve Size - Pressure in PSI | [5 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
| 3" | 6.612 | 7.054 |  | 3" | 6.612 | 7.054 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 4" Actuator | 65.4205 | 65.4205 | 36.7625 | 23.5124 | 16.3227 | 9.176
| 4" | 12.106 | 12.548 |  | 4" | 12.106 | 12.548 | Side Port (P2), Actuator Spring |  |  | 4LS" | 179.6783 | 196.9682 | 96.5071 | 53.1574 | 39.2626 | 23.9827 | 5" Actuator | 103.5824 | 103.5824 | 58.2072 | 37.2279 | 25.8442 | 14.5286
|  | w/o stem | w/ stem |  |  |  |  | Opens Stem Against: |  |  |  | 399.8828 | 441.2424 | 216.1924 | 130.5404 | 87.9548 | 47.4609 | 6" Actuator | 148.3295 | 148.3295 | 83.3525 | 53.3102 | 37.0088 | 20.8049
[11 empty] | 6LS" | 497.1556 | 520.0673 | 254.8137 | 147.0822 | 103.6674 | 60.3361
VALVE SPRING FORCE TABLE WITH 4"& 6" LONG STROKE | [17 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 20 | PSIG
Valve Type |  | Spring Rate | Pre-load | Pre-load | Stroke | Comp. | Comp. | Lower Port (P1), | 50 | psi Air | 4LS" | 192.5477 | 179.5999 | 100.9246 | 69.2024 | 44.8109 | 22.7419 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
|  | Lbs/in | Length | Force (lbs) | Length | Length | Force (lbs) | to air port B, will hold closed against: |  |  |  | 218.4542 | 187.4816 | 105.3536 | 67.3816 | 46.7774 | 26.854 | 4" Actuator | 130.8409 | 130.8409 | 73.5249 | 47.0247 | 32.6453 | 18.3519
4" LONG STROKE SPRING VALUES | [10 empty] | 6LS" | 378.5221 | 361.3643 | 212.7072 | 136.0423 | 90.1618 | 47.1008 | 5" Actuator | 207.1648 | 207.1648 | 116.4144 | 74.4558 | 51.6884 | 29.0572
W61/ 4" LS AR | 2.5 | 50 | 8.933 | 169.4325 | 1.845 | 7.088 | 257.07 | [10 empty] | 6" Actuator | 296.6591 | 296.6591 | 166.705 | 106.6204 | 74.0176 | 41.6098
W61/ 4" LS AR | 3 | 50 | 8.933 | 169.4325 | 2.323 | 6.61 | 279.775
W61/ 4" LS AR | 4 | 50 | 8.909 | 170.5725 | 3.159 | 5.75 | 320.625 | [10 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 32.6 | PSIG
W61/ 4" LS AL | 2.5 | 50 | 9.125 | 160.3125 | 1.873 | 7.252 | 249.28 | W62 Series Valves AR (Air-to-Raise) | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W61/ 4" LS AL | 3 | 50 | 9.125 | 160.3125 | 2.378 | 6.747 | 273.2675 |  |  |  | Actuator | Valve Size - Pressure in PSI | [5 empty] | 4" Actuator | 213.2707 | 213.2707 | 119.8456 | 76.6503 | 53.2119 | 29.9136
W61/ 4" LS AL | 4 | 50 | 9.125 | 160.3125 | 3.059 | 6.066 | 305.615 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 5" Actuator | 337.6786 | 337.6786 | 189.7555 | 121.3629 | 84.2521 | 47.3633
[8 empty] | Bottom Port (P1), Actuator |  |  | 4LS" | 91.3268 | 91.3268 | 51.3203 | 32.8232 | 22.7864 | 12.8096 | 6" Actuator | 483.5543 | 483.5543 | 271.7291 | 173.7912 | 120.6487 | 67.824
W61/ 5" AR | 1" | 323 | 4.704 | 465.1846 | 0.631 | 4.073 | 658.807 | Spring holds closed against: |  |  |  | 220.1213 | 220.1213 | 123.6952 | 79.1124 | 54.9211 | 31.827
W61/ 5" AR | 1.5-3" | 323 | 4.891 | 407.8037 | 0.818 | 4.073 | 658.807 |  |  |  | 6LS" | 311.783 | 311.783 | 175.2037 | 112.056 | 77.791 | 43.7311 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 40 | PSIG
W61/ 5" AR | 4" | 323 | 4.867 | 415.168 | 0.794 | 4.073 | 658.807 | [10 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W61/ 5" AL | 1" | 323 | 5.116 | 338.7624 | 0.704 | 4.412 | 554.7848 | Middle Side Port (P2), Air to actuator |  |  | 4LS" | 136.2724 | 145.2974 | 81.6486 | 48.9768 | 36.2523 | 23.4723 | 4" Actuator | 261.6818 | 261.6818 | 147.0498 | 94.0494 | 65.2906 | 36.7039
W61/ 5" AL | 1.5-3" | 323 | 5.116 | 338.7624 | 0.891 | 4.225 | 612.1658 | (with stem raised), spring will |  |  |  | 320.327 | 333.2461 | 187.2647 | 119.7699 | 83.1462 | 47.7173 | 5" Actuator | 414.3295 | 414.3295 | 232.8289 | 148.9116 | 103.3768 | 58.1144
W61/ 5" AL | 4" | 323 | 5.116 | 338.7624 | 0.867 | 4.249 | 604.8013 | lower against: |  |  | 6LS" | 374.7067 | 387.3417 | 217.6633 | 134.671 | 96.6432 | 58.6589 | 6" Actuator | 593.3182 | 593.3182 | 333.41 | 213.2408 | 148.0352 | 83.2196
6" LONG STROKE SPRING VALUES
W61/ 6" LS AR | 2.5 | 70 | 10.449 | 577.9515 | 1.873 | 8.576 | 702.506 | Middle Side Port (P2), Air @ |  | 50 | 4LS" | 314.8443 | 314.8443 | 154.262 | 93.1458 | 62.7593 | 34.2776 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 50 | PSIG
W61/ 6" LS AR | 3 | 70 | 10.449 | 595.2415 | 2.351 | 8.098 | 734.293 | psi to port A,will raise stem (opens)against: |  |  |  | 397.6567 | 397.6567 | 194.837 | 117.6457 | 79.2667 | 42.3063 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W61/ 6" LS AR | 4 | 70 | 10.425 | 579.88 | 3.187 | 7.238 | 791.483 |  |  |  | 6LS" | 574.0227 | 574.0227 | 281.2498 | 169.8231 | 114.4226 | 62.4948 | 4" Actuator | 327.1023 | 327.1023 | 183.8123 | 117.5618 | 81.6133 | 45.8798
W61/ 6" LS AL | 2.5 | 70 | 10.731 | 559.1985 | 1.963 | 8.768 | 689.738 | [10 empty] | 5" Actuator | 517.9119 | 517.9119 | 291.0361 | 186.1395 | 129.221 | 72.6431
W61/ 6" LS AL | 3 | 70 | 10.731 | 559.1985 | 2.441 | 8.29 | 721.525 | Upper Side Port (P3), Air @ |  | 50 | 4LS" | 254.826 | 242.7744 | 118.9504 | 75.3896 | 48.3933 | 23.2256 | 6" Actuator | 741.6477 | 741.6477 | 416.7625 | 266.5509 | 185.0439 | 104.0245
W61/ 6" LS AL | 4 | 70 | 10.731 | 559.1985 | 3.153 | 7.578 | 768.873 | to Port A, w/stem raised,will hold against: |  |  |  | 263.8464 | 246.5948 | 120.8223 | 72.9544 | 49.1549 | 25.8358
4" LONG STROKE SPRING VALUES | [10 empty] | 6LS" | 489.9971 | 473.1249 | 231.8136 | 144.9643 | 94.3101 | 47.022 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 60 | PSIG
W62/ 4" AR | 2.5 | 50 | 8.938 | 169.195 | 1.753 | 7.185 | 252.4625 | [10 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W62/ 4" AR | 3 | 50 | 8.938 | 169.195 | 2.105 | 6.833 | 269.1825 | [10 empty] | 4" Actuator | 392.5227 | 392.5227 | 220.5747 | 141.0741 | 97.9359 | 55.0558
W62/ 4" AR | 4 | 50 | 8.938 | 169.195 | 2.965 | 5.973 | 310.0325 | [10 empty] | 5" Actuator | 621.4943 | 621.4943 | 349.2433 | 223.3674 | 155.0652 | 87.1717
W62/ 4" AL | 2.5 | 50 | 8.938 | 169.195 | 1.753 | 7.185 | 252.4625 | W62 Series Valves AL (Air-to-Lower) | [9 empty] | 6" Actuator | 889.9773 | 889.9773 | 500.1149 | 319.8611 | 222.0527 | 124.8295
W62/ 4" AL | 3 | 50 | 8.938 | 169.195 | 2.105 | 6.833 | 269.1825 |  |  |  | Actuator | Valve Size - Pressure in PSI
W62/ 4" AL | 4 | 50 | 8.938 | 169.195 | 2.965 | 5.973 | 310.0325 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 70 | PSIG
[8 empty] | Bottom Port (P1), Air @ |  | 50 | 4LS" | 190.8299 | 181.8049 | 102.1637 | 68.585 | 45.361 | 22.4075 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W62/ 5" AR | 1" | 323 | 4.891 | 407.8037 | 0.605 | 4.286 | 593.4479 | Psi, Air to Port B, will hold against: |  |  |  | 187.4816 | 187.4816 | 105.3536 | 67.3816 | 46.7774 | 27.2489 | 4" Actuator | 457.9432 | 457.9432 | 257.3372 | 164.5865 | 114.2586 | 64.2318
W62/ 5" AR | 1.5-3" | 323 | 4.891 | 407.8037 | 0.683 | 4.208 | 617.3822 |  |  |  | 6LS" | 376.1171 | 363.4821 | 204.2556 | 135.1779 | 90.6902 | 46.6527 | 5" Actuator | 725.0767 | 725.0767 | 407.4505 | 260.5953 | 180.9094 | 101.7003
W62/ 5" AR | 4" | 323 | 4.85 | 420.3845 | 0.684 | 4.166 | 630.2699 | [10 empty] | 6" Actuator | 1038.3068 | 1038.3068 | 583.4674 | 373.1713 | 259.0615 | 145.6344
W62/ 5" AL | 1" | 323 | 4.83 | 426.5215 | 0.605 | 4.225 | 612.1658 | Middle Port (P2), (stem lowered), spring |  |  | 4LS" | 181.9722 | 194.0238 | 95.0645 | 53.836 | 38.6756 | 24.3293
W62/ 5" AL | 1.5-3" | 323 | 4.908 | 402.5872 | 0.683 | 4.225 | 612.1658 | opens stem against: |  |  |  | 441.2424 | 441.2424 | 216.1924 | 130.5404 | 87.9548 | 47.0515 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 77.3 | PSIG
W62/ 5" AL | 4" | 323 | 4.95 | 389.6995 | 0.684 | 4.266 | 599.5849 |  |  |  | 6LS" | 500.3671 | 517.2393 | 253.428 | 148.0323 | 103.1037 | 60.8006 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
6" LONG STROKE SPRING VALUES | [17 empty] | 4" Actuator | 505.7001 | 505.7001 | 284.1738 | 181.7505 | 126.1741 | 70.9302
W62/ 6" LS AR | 2.5 | 70 | 10.454 | 577.619 | 1.753 | 8.701 | 694.1935 | Middle Side Port (P2), Air @ |  | 50 | 4LS" | 235.7754 | 235.7754 | 132.4919 | 84.7386 | 58.8269 | 33.0702 | 5" Actuator | 800.6918 | 800.6918 | 449.9418 | 287.7716 | 199.7757 | 112.3062
W62/ 6" LS AR | 3 | 70 | 10.454 | 577.619 | 2.105 | 8.349 | 717.6015 | to port B, (w/stem raised), |  |  |  | 287.6873 | 300.6063 | 168.9231 | 108.039 | 75.0024 | 43.1392 | 6" Actuator | 1146.5874 | 1146.5874 | 644.3148 | 412.0878 | 286.0779 | 160.8219
W62/ 6" LS AR | 4 | 70 | 10.454 | 577.619 | 2.965 | 7.489 | 774.7915 | will close stem against: |  |  | 6LS" | 439.0409 | 439.0409 | 246.7152 | 157.7929 | 109.5424 | 61.5805
W62/ 6" LS AL | 2.5 | 70 | 10.454 | 577.619 | 1.753 | 8.701 | 694.1935 | [10 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 80 | PSIG
W62/ 6" LS AL | 3 | 70 | 10.454 | 577.619 | 2.105 | 8.349 | 717.6015 | Upper Side Port (P3), (stem raised) |  |  | 4LS" | 121.9539 | 121.9539 | 59.7529 | 36.0797 | 24.3096 | 13.2773 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W62/ 6" LS AL | 4 | 70 | 10.454 | 577.619 | 2.965 | 7.489 | 774.7915 | Actuator spring holds against: |  |  |  | 307.432 | 290.1805 | 142.1776 | 85.8491 | 57.843 | 30.5811 | 4" Actuator | 523.3636 | 523.3636 | 294.0996 | 188.0988 | 130.5812 | 73.4077
4" LONG STROKE SPRING VALUES | [10 empty] | 6LS" | 416.3415 | 416.3415 | 203.9918 | 123.1735 | 82.9912 | 45.3278 | 5" Actuator | 828.6591 | 828.6591 | 465.6577 | 297.8232 | 206.7536 | 116.2289
W63/ 4" AR | 2.5 | 50 | 9.215 | 156.0375 | 1.901 | 7.314 | 246.335 | [10 empty] | 6" Actuator | 1186.6364 | 1186.6364 | 666.8199 | 426.4815 | 296.0703 | 166.4393
W63/ 4" AR | 3 | 50 | 9.215 | 156.0375 | 2.446 | 6.769 | 272.2225
W63/ 4" AR | 4 | 50 | 9.215 | 156.0375 | 3.182 | 6.033 | 307.1825 | [10 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 90 | PSIG
W63/ 4" AL | 2.5 | 50 | 8.939 | 169.1475 | 1.851 | 7.088 | 257.07 | [10 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W63/ 4" AL | 3 | 50 | 8.911 | 170.4775 | 2.301 | 6.61 | 279.775 | W63 Series Valves AR (Air-to-Raise), Fail Open (Normally Open) | [9 empty] | 4" Actuator | 588.7841 | 588.7841 | 330.8621 | 211.6112 | 146.9039 | 82.5837
W63/ 4" AL | 4 | 50 | 8.965 | 167.9125 | 3.215 | 5.75 | 320.625 |  |  |  | Actuator | Valve Size - Pressure in PSI | [5 empty] | 5" Actuator | 932.2415 | 932.2415 | 523.8649 | 335.0511 | 232.5978 | 130.7575
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 6" Actuator | 1334.9659 | 1334.9659 | 750.1724 | 479.7917 | 333.0791 | 187.2442
W63/ 5" AR | 1" | 323 | 5.116 | 338.7624 | 0.643 | 4.473 | 536.067 | Bottom Port (P2), stem raised, |  |  | 4LS" | 132.9649 | 146.9383 | 82.5707 | 47.7881 | 36.6617 | 23.2566
W63/ 5" AR | 1.5-3" | 323 | 5.116 | 338.7624 | 0.908 | 4.208 | 617.3822 | Actuator spring will open against: |  |  |  | 289.3543 | 333.2461 | 187.2647 | 119.7699 | 83.1462 | 47.7173 | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 95 | PSIG
W63/ 5" AR | 4" | 323 | 5.116 | 338.7624 | 0.95 | 4.166 | 630.2699 |  |  |  | 6LS" | 365.2305 | 389.6031 | 218.9341 | 131.2652 | 97.2075 | 58.3518 | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W63/ 5" AL | 1" | 323 | 4.643 | 483.9024 | 0.57 | 4.073 | 658.807 | [10 empty] | 4" Actuator | 621.4943 | 621.4943 | 349.2433 | 223.3674 | 155.0652 | 87.1717
W63/ 5" AL | 1.5-3" | 323 | 4.908 | 402.5872 | 0.835 | 4.073 | 658.807 | Top Port (P1), | 50 | psi Air to | 4LS" | 259.2426 | 240.5832 | 117.8768 | 76.6962 | 47.9565 | 23.4493 | 5" Actuator | 984.0327 | 984.0327 | 552.9686 | 353.665 | 245.5199 | 138.0218
W63/ 5" AL | 4" | 323 | 4.95 | 389.6995 | 0.877 | 4.073 | 658.807 | port A, will hold valve closed against: |  |  |  | 305.2059 | 246.5948 | 120.8223 | 72.9544 | 49.1549 | 25.8358 | 6" Actuator | 1409.1307 | 1409.1307 | 791.8487 | 506.4468 | 351.5835 | 197.6466
6" LONG STROKE SPRING VALUES | [10 empty] | 6LS" | 502.6513 | 470.1051 | 230.334 | 148.7081 | 93.7082 | 47.3403
W63/ 6" LS AR | 2.5 | 70 | 10.731 | 559.1985 | 1.766 | 8.965 | 676.6375 | [10 empty] | Actuator | Holding Pressure Against Air Pressure= |  |  |  | 100 | PSIG
W63/ 6" LS AR | 3 | 70 | 10.731 | 559.1985 | 2.445 | 8.286 | 721.791 | W63 Series Valves AL (Air-to-Lower), Fail Closed (Normally Closed) | [9 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W63/ 6" LS AR | 4 | 70 | 10.731 | 559.1985 | 3.181 | 7.55 | 770.735 |  |  |  | Actuator | Valve Size - Pressure in PSI | [5 empty] | 4" Actuator | 654.2045 | 654.2045 | 367.6245 | 235.1235 | 163.2265 | 91.7596
W63/ 6" LS AL | 2.5 | 70 | 10.454 | 577.619 | 1.878 | 8.576 | 702.506 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 5" Actuator | 1035.8239 | 1035.8239 | 582.0722 | 372.2789 | 258.442 | 145.2861
W63/ 6" LS AL | 3 | 70 | 10.454 | 577.619 | 2.293 | 8.161 | 730.1035 | Top Port (P1), Actuator Spring |  |  | 4LS" | 121.9197 | 122.8783 | 60.2058 | 36.0696 | 24.4939 | 13.1767 | 6" Actuator | 1483.2955 | 1483.2955 | 833.5249 | 533.1019 | 370.0879 | 208.0491
W63/ 6" LS AL | 4 | 70 | 10.454 | 577.619 | 3.216 | 7.238 | 791.483 | Holds Closed Against: |  |  |  | 348.7916 | 290.1805 | 142.1776 | 85.8491 | 57.843 | 30.5811
4" LONG STROKE SPRING VALUES | [10 empty] | 6LS" | 416.3415 | 416.3415 | 203.9918 | 123.1735 | 82.9912 | 45.3278
W65/ 4" AR | 1" | - | - | #VALUE! | #VALUE! | - | #VALUE!
W65/ 4" AR | 1.5" | - | - | #VALUE! | #VALUE! | - | #VALUE! | Lower Port (P2), | 50 | psi Air | 4LS" | 235.8011 | 235.0832 | 132.1029 | 84.7478 | 58.6542 | 33.1673
W65/ 4" AR | 2" | - | - | #VALUE! | #VALUE! | - | #VALUE! | to port B, will open stem against: |  |  |  | 256.7146 | 300.6063 | 168.9231 | 108.039 | 75.0024 | 43.1392
W65/ 4" AR | 2.5" | 50 | 8.938 | 169.195 | 1.691 | 7.247 | 249.5175 |  |  |  | 6LS" | 439.0409 | 439.0409 | 246.7152 | 157.7929 | 109.5424 | 61.5805
W65/ 4" AR | 3" | 50 | 8.938 | 169.195 | 2.106 | 6.832 | 269.23
W65/ 4" AR | 4" | 50 | 8.938 | 169.195 | 2.133 | 6.805 | 270.5125
W65/ 4" AL | 1" | - | - | #VALUE! | #VALUE! | - | #VALUE!
W65/ 4" AL | 1.5" | - | - | #VALUE! | #VALUE! | - | #VALUE! | W65 Series Valves AR (Air-to-Raise)
W65/ 4" AL | 2" | - | - | #VALUE! | #VALUE! | - | #VALUE! |  |  |  | Actuator | Valve Size - Pressure in PSI
W65/ 4" AL | 2.5" | 50 | 8.938 | 169.195 | 1.691 | 7.247 | 249.5175 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W65/ 4" AL | 3" | 50 | 8.938 | 169.195 | 2.133 | 6.805 | 270.5125 | Middle Port (P1), Actuator |  |  | 4LS" | #VALUE! | #VALUE! | #VALUE! | 36.0797 | 24.3096 | 13.2773
W65/ 4" AL | 4" | 50 | 8.938 | 169.195 | 2.842 | 6.096 | 304.19 | Spring holds closed against: |  |  |  | 335.5212 | 289.0746 | 138.6015 | 87.3541 | 58.9011 | 32.4352
[11 empty] | 6LS" | #VALUE! | #VALUE! | #VALUE! | 123.1735 | 82.9912 | 45.3278
W65/ 5" AR | 1" | 323 | 4.703 | 465.4914 | 0.519 | 4.184 | 624.7466
W65/ 5" AR | 1.5" | 323 | 4.913 | 401.053 | 0.649 | 4.264 | 600.1986 | Lower Port (P3), Stem Raised |  |  | 4LS" | #VALUE! | #VALUE! | #VALUE! | 53.208 | 38.6825 | 21.2281
W65/ 5" AR | 2" | 323 | 4.941 | 392.4611 | 0.736 | 4.205 | 618.3027 | Spring lowers stem against: |  |  |  | 450.3105 | 432.6166 | 218.3597 | 131.8491 | 89.3657 | 49.3632
W65/ 5" AR | 2.5" | 323 | 4.885 | 409.6447 | 0.68 | 4.205 | 618.3027 |  |  |  | 6LS" | #VALUE! | #VALUE! | #VALUE! | 147.1531 | 103.1132 | 60.1587
W65/ 5" AR | 3" | 323 | 4.884 | 409.9516 | 0.691 | 4.193 | 621.985
W65/ 5" AR | 4" | 323 | 4.873 | 413.327 | 0.703 | 4.17 | 629.0425 | Top Port (P2), Air @ psi |  | 50 | 4LS" | #VALUE! | #VALUE! | #VALUE! | 93.1458 | 62.7593 | 34.2776
W65/ 5" AL | 1" | 323 | 4.932 | 395.2228 | 0.519 | 4.413 | 554.4779 | to port A, will raise stem against: |  |  |  | 356.076 | 402.5225 | 200.2554 | 117.2531 | 78.9581 | 42.8601
W65/ 5" AL | 1.5" | 323 | 4.852 | 419.7708 | 0.649 | 4.203 | 618.9165 |  |  |  | 6LS" | #VALUE! | #VALUE! | #VALUE! | 169.8231 | 114.4226 | 62.4948
W65/ 5" AL | 2" | 323 | 4.911 | 401.6667 | 0.736 | 4.175 | 627.5082
W65/ 5" AL | 2.5" | 323 | 4.91 | 401.9735 | 0.679 | 4.231 | 610.3247 | Middle Port (P1), Air @ |  | 50 | 4LS" | #VALUE! | #VALUE! | #VALUE! | 76.0176 | 48.3865 | 26.3269
W65/ 5" AL | 3" | 323 | 4.923 | 397.9844 | 0.686 | 4.237 | 608.4836 | to port A,(w/stem raised), will hold against: |  |  |  | 241.2866 | 258.9805 | 120.4972 | 72.7581 | 48.4935 | 25.9322
W65/ 5" AL | 4" | 323 | 4.946 | 390.9269 | 0.703 | 4.243 | 606.6425 |  |  |  | 6LS" | #VALUE! | #VALUE! | #VALUE! | 145.8436 | 94.3006 | 47.6639
6" LONG STROKE SPRING VALUES
W65/ 6" AR | 1" | - | - | #VALUE! | #VALUE! | - | #VALUE!
W65/ 6" AR | 1.5" | - | - | #VALUE! | #VALUE! | - | #VALUE!
W65/ 6" AR | 2" | - | - | #VALUE! | #VALUE! | - | #VALUE! | W65 Series Valves AL (Air-to-Lower)
W65/ 6" AR | 2.5" | 70 | 10.454 | 577.619 | 1.691 | 8.763 | 690.0705 |  |  |  | Actuator | Valve Size - Pressure in PSI
W65/ 6" AR | 3" | 70 | 10.454 | 577.619 | 2.106 | 8.348 | 717.668 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
W65/ 6" AR | 4" | 70 | 10.454 | 577.619 | 2.842 | 7.612 | 766.612 | Middle Port (P1), Air @ |  | 50 | 4LS" | #VALUE! | #VALUE! | #VALUE! | 76.0176 | 48.2022 | 23.6841
W65/ 6" AL | 1" | - | - | #VALUE! | #VALUE! | - | #VALUE! | to port B, will hold closed against: |  |  |  | 291.9355 | 245.4889 | 117.2462 | 74.4594 | 50.4334 | 27.69
W65/ 6" AL | 1.5" | - | - | #VALUE! | #VALUE! | - | #VALUE! |  |  |  | 6LS" | #VALUE! | #VALUE! | #VALUE! | 149.4687 | 96.7431 | 48.9979
W65/ 6" AL | 2" | - | - | #VALUE! | #VALUE! | - | #VALUE!
W65/ 6" AL | 2.5" | 70 | 10.454 | 577.619 | 1.691 | 8.763 | 690.0705 | Middle Port (P1), (stem raised), spring |  |  | 4LS" | #VALUE! | #VALUE! | #VALUE! | 36.0797 | 24.3096 | 13.2773
W65/ 6" AL | 3" | 70 | 10.454 | 577.619 | 2.106 | 8.348 | 717.668 | holds closed against: |  |  |  | 284.8723 | 302.5662 | 141.8525 | 85.7183 | 57.1817 | 30.6774
W65/ 6" AL | 4" | 70 | 10.454 | 577.619 | 2.842 | 7.612 | 766.612 |  |  |  | 6LS" | #VALUE! | #VALUE! | #VALUE! | 123.1735 | 82.9912 | 45.3278
[8 empty] | Lower Port (P3), Air @ psi |  | 50 | 4LS" | #VALUE! | #VALUE! | #VALUE! | 93.1458 | 62.7593 | 34.2776
[8 empty] | to port B, will lower stem against: |  |  |  | 406.7248 | 389.0309 | 197.0043 | 118.8889 | 80.6775 | 44.6179
[11 empty] | 6LS" | #VALUE! | #VALUE! | #VALUE! | 173.4482 | 116.8651 | 63.8288
[8 empty] | Upper Port (P2), stem lowered, |  |  | 4LS" | #VALUE! | #VALUE! | #VALUE! | 53.208 | 38.8667 | 23.8708
[8 empty] | Actuator spring raises stem against: |  |  |  | 399.6616 | 446.1082 | 221.6107 | 130.1478 | 87.4258 | 47.6053
| WAUKESHA-CHERRY SPECS |  |  |  | CHERRY VALVE SPECS | [5 empty] | 6LS" | #VALUE! | #VALUE! | #VALUE! | 147.1531 | 103.1132 | 60.1587
| Effective Plug Diameter |  |  |  | Effective Plug Diameter
| Line Size | Upper (in) | Lower (in) |  | Line Size | Upper (in) | Lower (in)
| 1" | 1.2954 | 1.497 |  | 1 1/2" | 1.2954 | 1.497
| 1 1/2" | 1.2954 | 1.497 |  | 2" | 1.8507 | 1.9969 | W64R Series Valves AR (Air-to-Raise), Fail Closed (Normally Closed)
| 2" | 1.8507 | 1.9969 |  | 2 1/2" | 2.3817 | 2.497 |  |  |  | Actuator | Valve Size - Pressure in PSI
| 2 1/2" | 2.3817 | 2.497 |  | 3" | 2.9015 | 2.9969 |  |  |  | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
| 3" | 2.9015 | 2.9969 |  | 4" | 3.926 | 3.9971 | Tank Port (P1), Actuator |  |  | 4LS" | 91.455 | 91.455 | 51.3924 | 32.8693 | 22.8184 | 12.9139
| 4" | 3.926 | 3.9971 |  |  | w/o stem | w/ stem | Spring holds closed against: |  |  |  | 251.094 | 220.1213 | 123.6952 | 79.1124 | 54.9211 | 31.4321
|  | w/o stem | w/ stem | [7 empty] | 6LS" | 311.9625 | 321.2951 | 175.3046 | 112.1205 | 80.1644 | 43.9023
| Actuator | AR | AL | SPRING |  | VOLUME |  | Side Port (P2), | 50 | psi Air | 4LS" | 314.6731 | 314.6731 | 154.1781 | 93.0952 | 62.7252 | 34.1695
| Size (in) | Area (in2) | Area (in2) | FREE LNG | RATE | AR | AL | to port A, will open against: |  |  |  | 356.2971 | 397.6567 | 194.837 | 117.6457 | 79.2667 | 42.7156
| 4" | 12.12 | 12.12 | 12.5 | 365 | 12.7 | 14 |  |  |  | 6LS" | 573.7831 | 561.3206 | 281.1324 | 169.7522 | 111.8906 | 62.3174
| 5" | 19.19 | 19.19 | 6.22 | 323 | 21.5 | 27.1
| 6" | 27.48 | 27.82 | 6.94 | 1198 | 31.2 | 33.1 | W64R Series Valves AL (Air-to-Lower), Fail Open (Normally Open)
[11 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[8 empty] | Side Port (P2), Actuator Spring |  |  | 4LS" | 179.6783 | 196.9682 | 96.5071 | 53.1574 | 39.2626 | 23.9827
[8 empty] | Opens Stem Against: |  |  |  | 399.8828 | 441.2424 | 216.1924 | 130.5404 | 87.9548 | 47.4609
[11 empty] | 6LS" | 497.1556 | 520.0673 | 254.8137 | 147.0822 | 103.6674 | 60.3361
[8 empty] | Tank Port (P1), | 50 | psi Air | 4LS" | 192.5477 | 179.5999 | 100.9246 | 69.2024 | 44.8109 | 22.7419
[8 empty] | to port B, will hold closed against: |  |  |  | 218.4542 | 187.4816 | 105.3536 | 67.3816 | 46.7774 | 26.854
[11 empty] | 6LS" | 378.5221 | 361.3643 | 203.0655 | 136.0423 | 90.1618 | 47.1008
W64 Series Valves AR (Air-to-Raise), Fail Open (Normally Open)
[11 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[8 empty] | Tank Port (P1), stem raised, |  |  | 4LS" | 132.9649 | 146.9383 | 82.5707 | 47.7881 | 36.6617 | 23.2566
[8 empty] | Actuator spring will open against: |  |  |  | 289.3543 | 333.2461 | 187.2647 | 119.7699 | 83.1462 | 47.7173
[11 empty] | 6LS" | 365.2305 | 389.6031 | 218.9341 | 131.2652 | 97.2075 | 58.3518
[8 empty] | Side Port (P2), | 50 | psi Air | 4LS" | 259.2426 | 240.5832 | 117.8768 | 76.6962 | 47.9565 | 23.4493
[8 empty] | to port A, will hold valve closed against: |  |  |  | 305.2059 | 246.5948 | 120.8223 | 72.9544 | 49.1549 | 25.8358
[11 empty] | 6LS" | 502.6513 | 470.1051 | 230.334 | 148.7081 | 93.7082 | 47.3403
W64 Series Valves AL (Air-to-Lower), Fail Closed (Normally Closed)
[11 empty] | Actuator | Valve Size - Pressure in PSI
[11 empty] | Size | 1" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
[8 empty] | Side Port (P2), Actuator Spring |  |  | 4LS" | 121.9197 | 122.8783 | 60.2058 | 36.0696 | 24.4939 | 13.1767
[8 empty] | Holds Closed Against: |  |  |  | 348.7916 | 290.1805 | 142.1776 | 85.8491 | 57.843 | 30.5811
[11 empty] | 6LS" | 416.3415 | 416.3415 | 203.9918 | 123.1735 | 82.9912 | 45.3278
[8 empty] | Tank Port (P1), | 50 | psi Air | 4LS" | 235.8011 | 235.0832 | 132.1029 | 84.7478 | 58.6542 | 33.1673
[8 empty] | to port B, will open stem against: |  |  |  | 256.7146 | 300.6063 | 168.9231 | 108.039 | 75.0024 | 43.1392
[11 empty] | 6LS" | 439.0409 | 439.0409 | 246.7152 | 157.7929 | 109.5424 | 61.5805

## CB w Tef-Flo
Cherry Burrell Style valves w/ Tef-flo seats
Stem Part Numbers for Tef-flo Seats
(Does not include the seat, for stems that include the Tef-flo seat part number starts with 2)
Size | M61 | M61 long stroke | M62 | M62 Long Stroke | Size | Tef-flo seats | Tef-flo P (Peek) seats
1.5 | 162-408X | 162-560X | 162-413X | 162-565X | 1 or 1.5 | 20-240 | 115347
2 | 162-409X | 162-561X | 162-414X | 162-566X | 2 | 20-241 | 115348
2.5 | 162-410X | 162-562X | 162-415X | 162-567X | 2.5 | 20-242 | 115349
3 | 162-411X | 162-563X | 162-416X | 162-568X | 3 | 20-243 | 115350
4 | 162-596X | 162-598X | 162-597X | n/a | 4 | 20-244 | 115351
Size | M81 | M81 long stroke | M82 | M82 Long Stroke
1.5 | 162-601X | 162-570X | 162-606X | 162-575X
2 | 162-602X | 162-571X | 162-607X | 162-576X
2.5 | 162-603X | 162-572X | 162-608X | 162-577X
3 | 162-604X | 162-573X | 162-609X | 162-578X
4 | 162-605X | n/a | 162-610X | n/a
Size | M91 | M91 long stroke | M92 | M92 Long Stroke
1.5 | 162-418X | 162-580X | 162-423X | 162-585X
2 | 162-419X | 162-581X | 162-424X | 162-586X
2.5 | 162-420X | 162-582X | 162-425X | 162-587X
3 | 162-421X | 162-583X | 162-426X | 162-588X
To convert to W-series Actuator
(need a W-series actuator with lower stem designed for for Cherry valves stems)
|  | AR | AL | AA
Complete 4" actuator assembly |  | ACT00120 | - | -
Complete 5" actuator assembly |  | ACT00119 | - | -
Lower actuator stem only, 4" valve |  | 113154
Lower actuator stem only, 5" valve |  | 113647